## Medium List ranked
Option | Option description | Score | Comment
4 | Lower the minimum frequency keeping threshold below 4 MW and have a national market for frequency keeping | 10 | Over the next 12-24 months, the Authority plans to look at the regulatory settings for encouraging competition in frequency regulation services as part of a separate project to the review of common quality requirements in Part 8 of the Code. This option will be considered as part of the work to be undertaken in that separate project.
5 | Allocate frequency keeping costs to the causers of frequency deviations | 10 | The Authority is looking at the regulatory settings for allocating frequency keeping costs as part of a separate project to the review of common quality requirements in Part 8 of the Code. This option will be considered as part of the work to be undertaken in that separate project.
3 | Procure more frequency keeping to manage frequency within the normal band (49.8–50.2 Hz), and procure more instantaneous reserve to keep frequency above 48 Hz for contingent events and above 47 Hz (in the North Island) and 45 Hz (in the South Island) for extended contingent events | 9 | No change to Part 8 of the Code is required for the system operator to implement this option. However, a Code-permitted deadband beyond which a generating station must contribute to managing / supporting frequency has implications for the system operator's procurement of frequency keeping and instantaneous reserves. Therefore, this option is included in the 'no regrets' frequency system studies to be undertaken by the system operator.
7 | Review the dispensations and equivalence arrangements framework (for frequency obligations) | 9 | The Authority will add a project to review the dispensations and equivalence arrangements to its prioritisation of projects for the financial year 1 July 2024 - 30 June 2025. Therefore, no consideration of this option is needed as part of the review of common quality requirements in Part 8 of the Code.
12 | Review the dispensations and equivalence arrangements framework (for voltage obligations) | 9 | The Authority will add a project to review the dispensations and equivalence arrangements to its prioritisation of projects for the financial year 1 July 2024 - 30 June 2025. Therefore, no consideration of this option is needed as part of the review of common quality requirements in Part 8 of the Code.
21 | New / amended / obsolete definitions are identified and addressed as part of the work on the common quality issues | 9 | The high ranking of this option is consistent with feedback received in submissions on the Common Quality Issues Paper.
35 | Remove the obligation on the system operator to eliminate from the power system any deviations from New Zealand standard time caused by variations in system frequency | 7
8 | Assign voltage support obligations to distributed energy resources (eg, by revising the 'point of connection' definition) | 6 | This option is included in the 'no regrets' voltage system studies to be undertaken by the system operator.
9 | Manage the import and export of reactive power at a GXP (eg, by revising the GXP power factors distributors must maintain, as specified in the Connection Code) | 6 | This option is included in the 'no regrets' voltage system studies to be undertaken by the system operator.
19 | Where a flexibility provider is providing a service to an asset owner, leave it to the flexibility provider rather than the asset owner to provide the network operator with the information required by the network operator to use the flexibility service | 6
14 | Asset owners (grid-connected parties, grid owners, and embedded generators) are made responsible for managing the harmonics caused by their asset(s) | 5 - 6
1 | Lower the 30 MW threshold for generating stations to be excluded by default from complying with the frequency-related asset owner performance obligations (AOPOs) referred to in cause 8.21 of the Code | 4 | This option is included in the 'no regrets' frequency system studies to be undertaken by the system operator.
10 | Lower the 30MW threshold for generating stations to be excluded by default from complying with the fault ride through obligations referred to in cause 8.21 of the Code | 4 | This option is included in the 'no regrets' voltage system studies to be undertaken by the system operator.
11 | Require alignment of voltage-related connection standards across distribution networks | 4 | The Authority will consider this option as part of a separate project that is reviewing the regulatory settings for distribution networks. Therefore, no consideration of this option is needed as part of the review of common quality requirements in Part 8 of the Code.
13 | Locate up-to-date standard(s) for harmonics in one piece of legislation / regulation (eg, the Electricity Industry (Safety) Regulations 2010 or the Code) | 4 | Note the wording of this option has been amended slightly to refer to "up-to-date" harmonics standard(s).
15 | Remove the first-mover advantage associated with total harmonic distortion (THD) by requiring the first mover to give up some of their share of THD | 4
16 | Lower the deminimis for generating stations to provide real time operational data to the system operator, and require the same information to be provided to distribution network operators in relation to embedded generating stations | 4 | Relevant Code provision is clause 8.25(6), which says if the system operator reasonably considers it necessary to assist it in planning to comply, and complying, with the principal performance obligations and achieving the dispatch objective, the system operator may apply to the Authority to require an embedded generator to provide information regarding the intended output of a group of embedded generating stations that total greater than 10 MW in capacity and that are connected to the same grid exit point. If the Authority approves the system operator’s request, the information must be provided to the system operator by the relevant embedded generator in a form and manner determined by the Authority. An embedded generator means a generator who owns or operates 1 or more embedded generating stations. An embedded generating station means 1 or more generating units that are directly connected to a local network or an embedded network and that injects into a local network or an embedded network at a single point of injection.
18 | Require wind generation to undertake periodic testing and provide results to system operator and distribution network operators so they can keep their models up to date | 4 | Relevant Code provision is clause 1 of Appendix B of Technical Code A of Schedule 8.3, which says for the purposes of Appendix B (Routine testing of assets and automatic under-frequency load shedding systems), generating unit does not include a generating unit for which wind is the primary power source.
39 | Require asset owners (grid-connected parties, grid owners, and embedded generators) to provide asset capability information, encrypted if required by the asset owner or its vendor, that network owners require to optimise their network investments | 4
2 | Set a permitted dead band beyond which a generation station must contribute to frequency keeping and instantaneous reserve | 3 | This option is included in the 'no regrets' frequency system studies to be undertaken by the system operator.
17 & 20 | Require asset owners (grid-connected parties, grid owners, and embedded generators) to provide asset capability information that network operators require to meet their regulatory obligations. This includes asset owners providing network operators with sufficiently detailed information so that there is no "black box" when the network operator comes to use the information for equipment performance assessment and checking compliance with technical requirements on the asset owner set out in the Code (eg, the system operator checking compliance with technical requirements in Part 8 of the Code) | 2
6 | Put in place ramping limits on generation plant for post-disturbance or change-of-MW output (eg, due to wind gust or cloud covering) | 0

## Medium List evaluated
| Option description | Reason for retaining in medium list | Evaluation criterion 2 | Evaluation criterion 3 | Evaluation criterion 4 | Evaluation criterion 5 | Evaluation criterion 6 | Evaluation criterion 7 | Score
Issue 1 • An increasing amount of variable and intermittent resources, primarily in the form of wind and solar PV generation, is likely to cause more frequency fluctuations, which are likely to be exacerbated over time by decreasing system inertia
1 | Lower the 30 MW threshold for generating stations to be excluded by default from complying with the frequency-related asset owner performance obligations (AOPOs) referred to in cause 8.21 of the Code | Moderately feasible with low risk of unintended consequences (<2 years to change the Code, <3 years to change assets, <$20m implementation cost) | Two ticks Moderately promotes one or more limbs of the Authority's statutory objective Implementation cost = approx $20m Annual frequency keeping costs double from $1m per month to $2m per month through doubling the FK from (2x 15MW) to (2 x 30 MW) Assume no deadbands therefore some residual O&M costs on generators due to governor response | Two ticks Yes | One tick Somewhat Non marginal cost pricing with some costs allocated to some causers | Two crosses No | One cross No | Two ticks Depending on the threshold, this option may not be durable under a scenario of large uptake of small-scale generation (eg, solar PV, batteries) because this SSDG would still be excluded from the frequency-related AOPOs | 4
2 | Set a permitted dead band beyond which a generating station must contribute to frequency keeping and instantaneous reserve | Feasible with uncertain risk of unintended consequences | One tick Weakly promotes one or more limbs of the Authority's statutory objective Assuming counterfactual is no deadband per current Code Costs will be placed on parties without a deadband who have responsive generating units Frequency support ancillary service costs will increase, paid for by purchasers under the status quo arrangements | Two ticks Yes | One tick Somewhat Non marginal cost pricing with some costs, in the form of additional frequency support ancillary service costs, allocated to some beneficiaries (ie, purchasers) | Two crosses No | One cross No | Two ticks This option may not be durable if the deadband is set at a level that necessitates a frequency keeping requirement that exceeds the amount of frequency keeping capability | 3
3 | Procure more frequency keeping to manage frequency within the normal band (49.8–50.2 Hz), and procure more instantaneous reserve to keep frequency above 48 Hz for contingent events and above 47 Hz (in the North Island) and 45 Hz (in the South Island) for extended contingent events | Strongly feasible with no risk of unintended consequences (<1 year to change the Code, <2 years to change assets, <$10m implementation cost) | Two ticks Moderately promotes one or more limbs of the Authority's statutory objective Implementation cost = negligible Annual frequency keeping costs double from $1m per month to $2m per month through doubling the FK from (2x 15MW) to (2 x 30 MW) Annual fast instantaneous reserves costs double (eg, $1m per month to $2m per month) Assume the status quo of no deadbands therefore some residual O&M costs on generators due to governor response Assume the status quo of no national frequency keeping market (such a market might be expected to reduce overall frequency keeping costs through competition) Reduced O&M costs for frequency sensitive load and generation - unquantified Improved productivity from frequency sensitive load and generation (less tripping of load and generation) - unquantified | One tick Somewhat (geothermal not conducive to frequency keeping operations) | One tick Somewhat Marginal cost pricing exists to that extent the reserves and energy are co-optimised Non marginal cost pricing exists to the extent that: a) additional frequency support ancillary service costs are allocated to some beneficiaries (ie, purchasers) b) instantaneous reserves costs are allocated to causers of underfrequency events | Two ticks Yes | One tick Somewhat | Two ticks | 9
4 | Lower the minimum frequency keeping threshold below 4 MW and have a national market for frequency keeping | Moderately feasible with low risk of unintended consequences (<2 years to change the Code, <3 years to change assets, <$20m implementation cost) | Two ticks Moderately promotes one or more limbs of the Authority's statutory objective Implementation cost expected to be low relative to the benefits over 30 years Annual benefits likely to be small while pool of < 4 MW frequency keeper providers is small | Two ticks Yes | One tick Somewhat Half-hourly frequency keeping offers are used but with non marginal cost pricing used in allocating frequency keeping ancillary service costs to some beneficiaries (ie, purchasers) | Two ticks Yes | One tick Somewhat | Two ticks | 10
5 | Allocate frequency keeping costs to the causers of frequency deviations | Moderately feasible with low risk of unintended consequences (<2 years to change the Code, <3 years to change assets, <$20m implementation cost) | Two ticks Moderately promotes one or more limbs of the Authority's statutory objective Implementation cost < $ 5m Under pro-rata sharing of frequency keeping costs between generation and load causers, assume frequency keeping cost saving of $100k - $250k per month being 10% - 25% of counterfactual which is a doubling from $1m per month to $2m per month through doubling the FK from (2x 15MW) to (2 x 30 MW) due to increased variability and intermittency of generation Assume the status quo of no deadbands therefore some residual O&M costs on generators due to governor response Assume the status quo of no national frequency keeping market (such a market might be expected to reduce overall frequency keeping costs through competition) | Two ticks Yes | One tick Somewhat Non marginal cost pricing and costs allocated to causers | One tick Yes By using causer pays approach, we are trying to minimise the need for frequency keeping support by financially incentivising those who cause frequency deviations to minimise such deviations | Two ticks Yes | Two ticks | 10
6 | Put in place ramping limits on generation plant for post-disturbance or change-of-MW output (eg, due to wind gust or cloud covering) | Moderately feasible with low risk of unintended consequences (<2 years to change the Code, <3 years to change assets, <$20m implementation cost) | One tick Weakly promotes one or more limbs of the Authority's statutory objective Assume this option is practically-speaking more relevant to overfrequency issue since would be very expensive for inverter-based resources to manage sudden reductions in generation caused by wind drop off and cloud cover increase - eg, through installing batteries Assume < $10m implementation cost from changing control systems on inverter-based resources for managing over-frequency Uncertain of benefit received from lower frequency keeping costs and O&M costs related to governor response | One cross Little | One tick Somewhat Non marginal cost pricing and costs allocated to causers | Two crosses No, because this is a perfornance standard | One cross No | Two ticks | 0
7 | Review the dispensations and equivalence arrangements framework (for frequency obligations) | Feasible with uncertain risk of unintended consequences | Two ticks Moderately promotes one or more limbs of the Authority's statutory objective Implementation cost < $ 1m Uncertain benefit - expected to be higher over time as, under the counterfactual, the system operator is likely to be unable to meet its PPOs under current framework | Two ticks Yes | One tick Somewhat Non marginal cost pricing and costs allocated to causers | One tick Yes Through the review of the dispensation and equivalence arrangements, we are trying to reduce the need for common quality support by requiring those who cause common quality issues to lessen the impact of those issues | One tick Somewhat | Two ticks | 9
Issues 2, 3, 4 • An increasing amount of variable and intermittent resources, primarily in the form of wind and solar PV generation, is likely to cause greater voltage deviations, which are exacerbated by changing patterns of reactive power flows • Increasing amounts of inverter-based variable and intermittent resources will reduce the transmission network’s system strength thereby increasing the likelihood of network performance issues due to inverter-based resources disconnecting from the power system • Over time increasingly less generation capacity is expected to be subject to fault ride through obligations in the Code, as more generating stations export less than 30 MW to a network
8 | Assign voltage support obligations to distributed energy resources (eg, by revising the 'point of connection' definition) | Moderately feasible with low risk of unintended consequences (<2 years to change the Code, <3 years to change assets, <$20m implementation cost) | Two ticks Moderately promotes one or more limbs of the Authority's statutory objective Implementation cost assumed to be < $10m Ongoing cost = opportunity cost of foregone energy sales from having higher reactive power output requirement Unclear what this opportunity cost is, but assume this cost is recovered by being priced into energy price offers | Two ticks Yes | One tick Somewhat Non marginal cost pricing and costs allocated to causers | Two crosses No, because this is a perfornance standard | One tick Somewhat Theoretically DER could club together and ask network owners to install reactive power management devices | Two ticks | 6
9 | Manage the import and export of reactive power at a GXP (eg, by revising the GXP power factors distributors must maintain, as specified in the Connection Code) | Moderately feasible with low risk of unintended consequences (<2 years to change the Code, <3 years to change assets, <$20m implementation cost) | Two ticks Moderately promotes one or more limbs of the Authority's statutory objective Implementation cost assumed to be < $10m, on the assumption that distributors place an obligation, through their connecction and operation standards, on DER to support voltage This assumption is on the basis that distributors consider this approach to be lower cost than installing reactive power management devices on their networks in response to increased DER Ongoing cost = opportunity cost of foregone energy sales from having higher reactive power output requirement Unclear what this opportunity cost is, but assume this cost is recovered by being priced into energy price offers | Two ticks Yes, on the assumption that distributors place an obligation, through their connecction and operation standards, on DER to support voltage | One tick Somewhat Non marginal cost pricing and costs allocated to causers, on the assumption that distributors place an obligation, through their connecction and operation standards, on DER to support voltage | Two crosses No, because this is a perfornance standard | One tick Somewhat | Two ticks | 6
10 | Lower the 30MW threshold for generating stations to be excluded by default from complying with the fault ride through obligations referred to in cause 8.21 of the Code | Moderately feasible with low risk of unintended consequences (<2 years to change the Code, <3 years to change assets, <$20m implementation cost) | Two ticks Moderately promotes one or more limbs of the Authority's statutory objective Provides improved certainty in relation to system security should there be a grid fault / grid event, thereby reducing the possibility of lost load | Two ticks Yes | One tick Somewhat Non marginal cost pricing with some costs allocated to some causers | Two crosses No | One cross No | Two ticks Depending on the threshold, this option may not be durable under a scenario of large uptake of small-scale distributed generation (eg, solar PV, batteries) because this SSDG would still be excluded from the fault ride through AOPOs | 4
11 | Require alignment of voltage-related connection standards across distribution networks | Moderately feasible with low risk of unintended consequences (<2 years to change the Code, <3 years to change assets, <$20m implementation cost) | Two ticks Moderately promotes one or more limbs of the Authority's statutory objective Benefits are reduced transaction costs and implementation costs for DG wanting to connect across multiple distribution networks Assume the standards reflect differing DG capacities and possibly differing network characteristics (eg, urban / rural, high residential concentration vs high commercial/industrial concentration) | Two ticks Yes | One tick Somewhat Non marginal cost pricing with lower costs from standardisation allocated to beneficiaries, being the connecting DERs | Two crosses No | One cross No | Two ticks Assume the standards reflect differing DG capacities and possibly differing network characteristics (eg, urban / rural, high residential concentration vs high commercial/industrial concentration) | 4
12 | Review the dispensations and equivalence arrangements framework (for voltage obligations) | Feasible with uncertain risk of unintended consequences | Two ticks Moderately promotes one or more limbs of the Authority's statutory objective Implementation cost < $ 1m Uncertain benefit - expected to be higher over time as, under the counterfactual, the system operator is likely to be unable to meet its PPOs under current framework | Two ticks Yes | One tick Somewhat Non marginal cost pricing and costs allocated to causers | One tick Yes Through the review of the dispensation and equivalence arrangements, we are trying to reduce the need for common quality support by requiring those who cause common quality issues to lessen the impact of those issues | One tick Somewhat | Two ticks | 9
Issue 5 • There is some ambiguity around the applicability of harmonics standards and who manages harmonics (including the allocation of harmonics)
13 | Locate up-to-date standard(s) for harmonics in one piece of legislation / regulation (eg, the Electricity Industry (Safety) Regulations 2010 or the Code) | Strongly feasible with no risk of unintended consequences (<1 year to change the Code, <2 years to change assets, <$10m implementation cost) | Two ticks Moderately promotes one or more limbs of the Authority's statutory objective Greater clarity as to which harmonics standards apply to whom | Two ticks Yes | One tick Somewhat Non marginal cost pricing and costs allocated to causers | Two crosses No, because this is a perfornance standard | One cross No | Two ticks | 4
14 | Asset owners (grid-connected parties, grid owners, and embedded generators) are made responsible for managing the harmonics caused by their asset(s) | Strongly feasible with no risk of unintended consequences (<1 year to change the Code, <2 years to change assets, <$10m implementation cost) | One tick in short term (uncertain expected net benefit) because harmonics not causing significant issues at present Two ticks in longer term as harmonics cause issues for power system operation (including their potential to adversely affect (ie, limit) available network capacity Assume counterfactual is continued use of outdated harmonics standards, which means implementation cost of this option is estimated to be <$10m | Two ticks Yes | One tick Somewhat Non marginal cost pricing and costs allocated to causers | Two crosses No, because this is a perfornance standard | One tick Somewhat Theoretically embedded generators could club together and ask network owners to install harmonics filters | Two ticks | 5 - 6
15 | Remove the first-mover advantage associated with total harmonic distortion (THD) by requiring the first mover to give up some of their share of THD | The Authority understands that Transpower, as a grid owner, is looking at this matter. The Authority is unaware of what, if any, work is being done by distributors on this matter. | Two ticks Moderately promotes one or more limbs of the Authority's statutory objective Implementation cost expected to be measured in hundreds of thousands of dollars, being the cost of developing and implementing a harmonics allocation methodology Ongoing benefit should outweigh ongoing cost: Ignore wealth transfers from first mover having to invest in managing harmonics distortion thereby reducing some of the second mover's investment in managing harmonics distortion / first and second movers having to invest in managing harmonics distortion thereby reducing some of the third mover's investment in managing harmonics distortion / and so on; Net effect is some improvement in the efficient operation of the electricity industry from less distortion of generation investment / operating decisions | Two ticks Yes | One tick Somewhat Non marginal cost pricing and costs allocated to causers | Two crosses No | One cross No | Two ticks | 4
Issue 6 • Network operators have insufficient information on assets wanting to connect, or which are connected, to the power system to provide for the planning and operation of the power system in a safe, reliable, and economically efficient manner
16 | Lower the deminimis for generating stations to provide real time operational data to the system operator, and require the same information to be provided to distribution network operators in relation to embedded generating stations | Moderately feasible with low risk of unintended consequences (<2 years to change the Code, <3 years to change assets, <$20m implementation cost) Note that, after further consideration, the Authority has amended the reason for retaining this option in the medium list from the reason given to the CQTG meeting of 6 July 2023 (which was 'Feasible with uncertain risk of unintended consequences) | Two ticks Moderately promotes one or more limbs of the Authority's statutory objective Assume a de minimis of 10 MW across all grid-connected generation and embedded/distributed generation More accurate security assessments, which enable the system operator: 1) to plan to comply with its principal performance obligations in a more economically efficient manner, and 2) to achieve the system operator’s dispatch objective in a more economically efficient manner | Two ticks Yes | One tick Somewhat Non marginal cost pricing and costs allocated to causers | Two crosses No | One cross No | Two ticks Depending on the threshold, this option may not be durable under a scenario of large uptake of small-scale distributed generation (eg, solar PV, batteries) because this SSDG would still not need to provide the information | 4
17 & 20 | Require asset owners (grid-connected parties, grid owners, and embedded generators) to provide asset capability information that network operators require to meet their regulatory obligations. This includes asset owners providing network operators with sufficiently detailed information so that there is no "black box" when the network operator comes to use the information for equipment performance assessment and checking compliance with technical requirements on the asset owner set out in the Code (eg, the system operator checking compliance with technical requirements in Part 8 of the Code) | Feasible with uncertain risk of unintended consequences | Two ticks Moderately promotes one or more limbs of the Authority's statutory objective Assume no change to the current de minimis's for the provision of information, but rather the provision of sufficiently detailed information so that there is no 'black box' when the network operator comes to use the information for equipment performance assessment and checking compliance with technical requirements in the Code More accurate security assessments, which enable the system operator: 1) to plan to comply with its principal performance obligations in a more economically efficient manner, and 2) to achieve the system operator’s dispatch objective in a more economically efficient manner | Two ticks Yes | One tick Somewhat Non marginal cost pricing and costs allocated to beneficiaries, being the asset owners wanting to connect to the power system | Two crosses No | One cross No | - The option's durability is uncertain in an uncertain future scenario whereby vendors threaten to not supply the New Zealand electricity market because of concerns about intellectual property becoming known to competitors | 2
18 | Require wind generation to undertake periodic testing and provide results to system operator and distribution network operators so they can keep their models up to date | Strongly feasible with no risk of unintended consequences (<1 year to change the Code, <2 years to change assets, <$10m implementation cost) | Two ticks Moderately promotes one or more limbs of the Authority's statutory objective Cost measured in hundreds of thoursands of dollars per wind farm so total $5m Benefit is greater certainty that asset is able to operate to its capability | Two ticks Yes | One tick Somewhat Non marginal cost pricing and costs allocated to beneficiaries, being the asset owners wanting to connect to the power system | Two crosses No | One cross No | Two ticks | 4
19 | Where a flexibility provider is providing a service to an asset owner, leave it to the flexibility provider rather than the asset owner to provide the network operator with the information required by the network operator to use the flexibility service | Moderately feasible with low risk of unintended consequences (<2 years to change the Code, <3 years to change assets, <$20m implementation cost) | One tick Weakly promotes one or more limbs of the Authority's statutory objective Question whether this is necessary because flexibility providers will have to provide this information to provide an ancillary service | Two ticks Yes | One tick Somewhat Non marginal cost pricing and costs allocated to beneficiaries, being the flexibility providers and asset owners using the flexibility traders (assuming the asset owners are charged a fee by the flexibliity traders) | Two crosses No | Two ticks Yes Because either the asset owner or the flexiibility provider can provide the information required by the network operator | Two ticks | 6
Issue 7 • The Code is missing some terms that would help enable technologies, and contains some terms that appear to not be fit for the purpose of appropriately enabling technologies
21 | New / amended / obsolete definitions are identified and addressed as part of the work on the above 6 issues | Moderately feasible with low risk of unintended consequences (<2 years to change the Code, <3 years to change assets, <$20m implementation cost) | Two ticks Moderately promotes one or more limbs of the Authority's statutory objective Is possible that this option could be three ticks / strongly promotes the Authority's objectives if revised terminology enabled technologies that introduced more competition into the wholesale electricity market, including the spot market, ancillary services markets and hedge market | Two ticks Yes | One tick On the basis that this option supports the signalling of marginal costs and benefits | One tick On the basis that this option supports market-based approaches | One tick On the basis that this option supports output-based approaches | Two ticks | 9

## Medium List
| Option description | Reason for retaining in long list
Issue 1 • An increasing amount of variable and intermittent resources, primarily in the form of wind and solar PV generation, is likely to cause more frequency fluctuations, which are likely to be exacerbated over time by decreasing system inertia
1 | Lower the 30 MW threshold for generating stations to be excluded by default from complying with the frequency-related asset owner performance obligations (AOPOs) referred to in cause 8.21 of the Code | Moderately feasible with low risk of unintended consequences (<2 years to change the Code, <3 years to change assets, <$20m implementation cost)
2 | Set a permitted dead band beyond which a generating station must contribute to frequency keeping and instantaneous reserve | Feasible with uncertain risk of unintended consequences
3 | Procure more frequency keeping to manage frequency within the normal band (49.8–50.2 Hz), and procure more instantaneous reserve to keep frequency above 48 Hz for contingent events and above 47 Hz (in the North Island) and 45 Hz (in the South Island) for extended contingent events | Strongly feasible with no risk of unintended consequences (<1 year to change the Code, <2 years to change assets, <$10m implementation cost)
4 | Lower the minimum frequency keeping threshold below 4 MW and have a national market for frequency keeping | Moderately feasible with low risk of unintended consequences (<2 years to change the Code, <3 years to change assets, <$20m implementation cost)
5 | Allocate frequency keeping costs to the causers of frequency deviations | Moderately feasible with low risk of unintended consequences (<2 years to change the Code, <3 years to change assets, <$20m implementation cost)
6 | Put in place ramping limits on generation plant for post-disturbance or change-of-MW output (eg, due to wind gust or cloud covering) | Moderately feasible with low risk of unintended consequences (<2 years to change the Code, <3 years to change assets, <$20m implementation cost)
7 | Review the dispensations and equivalence arrangements framework | Feasible with uncertain risk of unintended consequences
Issues 2, 3, 4 • An increasing amount of variable and intermittent resources, primarily in the form of wind and solar PV generation, is likely to cause greater voltage deviations, which are exacerbated by changing patterns of reactive power flows • Increasing amounts of inverter-based variable and intermittent resources will reduce the transmission network’s system strength thereby increasing the likelihood of network performance issues due to inverter-based resources disconnecting from the power system • Over time increasingly less generation capacity is expected to be subject to fault ride through obligations in the Code, as more generating stations export less than 30 MW to a network
8 | Assign voltage support obligations to distributed energy resources (eg, by revising the 'point of connection' definition) | Moderately feasible with low risk of unintended consequences (<2 years to change the Code, <3 years to change assets, <$20m implementation cost)
9 | Manage the import and export of reactive power at a GXP (eg, by revising the GXP power factors distributors must maintain, as specified in the Connection Code) | Moderately feasible with low risk of unintended consequences (<2 years to change the Code, <3 years to change assets, <$20m implementation cost)
10 | Lower the 30MW threshold for generating stations to be excluded by default from complying with the fault ride through obligations in the Code | Moderately feasible with low risk of unintended consequences (<2 years to change the Code, <3 years to change assets, <$20m implementation cost)
11 | Require alignment of voltage-related connection standards across distribution networks | Moderately feasible with low risk of unintended consequences (<2 years to change the Code, <3 years to change assets, <$20m implementation cost)
12 | Review the dispensations and equivalence arrangements framework | Feasible with uncertain risk of unintended consequences
Issue 5 • There is some ambiguity around the applicability of harmonics standards and who manages harmonics (including the allocation of harmonics)
13 | Locate the standard(s) for harmonics in one piece of legislation / regulation (eg, the Electricity Industry (Safety) Regulations 2010 or the Code) | Strongly feasible with no risk of unintended consequences (<1 year to change the Code, <2 years to change assets, <$10m implementation cost)
14 | Asset owners (grid-connected parties, grid owners, and embedded generators) are made responsible for managing the harmonics caused by their asset(s) | Strongly feasible with no risk of unintended consequences (<1 year to change the Code, <2 years to change assets, <$10m implementation cost)
15 | Remove the first-mover advantage associated with total harmonic distortion (THD) by requiring the first mover to give up some of their share of THD | The Authority understands that Transpower, as a grid owner, is looking at this matter. The Authority is unaware of what, if any, work is being done by distributors on this matter.
Issue 6 • Network operators have insufficient information on assets wanting to connect, or which are connected, to the power system to provide for the planning and operation of the power system in a safe, reliable, and economically efficient manner
16 | Lower the deminimis for generating stations to provide real time operational data to the system operator, and require the same information to be provided to distribution network operators in relation to embedded generating stations | Feasible with uncertain risk of unintended consequences
17 | Require asset owners (grid-connected parties, grid owners, and embedded generators) to provide asset capability information required for network operators to meet their regulatory obligations | Moderately feasible with low risk of unintended consequences (<2 years to change the Code, <3 years to change assets, <$20m implementation cost)
18 | Require wind generation to undertake periodic testing and provide results to system operator and distribution network operators so they can keep their models up to date | Strongly feasible with no risk of unintended consequences (<1 year to change the Code, <2 years to change assets, <$10m implementation cost)
19 | Where a flexibility provider is providing a service to an asset owner, leave it to the flexibility provider rather than the asset owner to provide the network operator with the information required by the network operator to use the flexibility service | Moderately feasible with low risk of unintended consequences (<2 years to change the Code, <3 years to change assets, <$20m implementation cost)
20 | Require asset owners to provide system operator with sufficiently detailed information so that there is no "black box" when the system operator comes to use the information for equipment performance assessment and checking compliance with the Part 8 technical requirements | Feasible with uncertain risk of unintended consequences
Issue 7 • The Code is missing some terms that would help enable technologies, and contains some terms that appear to not be fit for the purpose of appropriately enabling technologies
21 | New / amended / obsolete definitions are identified and addressed as part of the work on the above 6 issues | Moderately feasible with low risk of unintended consequences (<2 years to change the Code, <3 years to change assets, <$20m implementation cost)

## Long List - CQTG additions
| Option description | Evaluation criterion 1 | Evaluation criterion 2 | Evaluation criterion 3 | Evaluation criterion 4 | Evaluation criterion 5 | Evaluation criterion 6 | Evaluation criterion 7 | Score
Issue 1 • An increasing amount of variable and intermittent resources, primarily in the form of wind and solar PV generation, is likely to cause more frequency fluctuations, which are likely to be exacerbated over time by decreasing system inertia
34 | Increase, from 45 Hz to 47 Hz, the minimum frequency at which South Island generation assets must remain synchronised for 30 seconds following an underfrequency event | Feasible but expensive or has long implementation and/or moderate risk of unintended consequences (> 3 year code change, > 5 year asset change, > $50m). Raising to 47 Hz will require a change to the design of the AUFLS regime for the South Island and to the system operator's system tools (eg, RMT). Would need to procure more reserves to cover HVDC ECEs. May lead to more frequency fluctuations because of more variable and intermittent generation connecting in the South Island (all else being equal). Also unclear the extent to which this option addresses the problem of more frequency fluctuations, which are likely to be exacerbated over time by decreasing system inertia, as a result of increasing amounts of variable and intermittent generation connecting t the power system. | Not applicable | Not applicable | Not applicable | Not applicable | Not applicable | Not applicable | Not applicable
35 | Remove the obligation on the system operator to eliminate from the power system any deviations from New Zealand standard time caused by variations in system frequency | Moderately feasible with low risk of unintended consequences (<2 years to change the Code, <3 years to change assets, <$20m implementation cost) | Two ticks Moderate Benefit is avoiding running generation higher relative to load (ie, generation MW > load MW) for periods of time necessary to get time error back to zero where the time error is negative. If time error has a normal distribution, the cost of running generation a little higher relative to load for 50% of the time will likely be greater than the cost savings from running generation lower relative to load (ie, generation MW < load MW) Costs (which fall on consuemrs) are uncertain (digital clocks linked to system frequency anecdotally appear to lose time accuracy for reasons other than time error due to variations in frequency from 50 Hz). But low risk of unintended consequences because consumers can set time against computers and smart phones (which are synchoronsied in accordance with the Network Time Protocol (NTP), which is a mechanism for synchronising the time on computers. The full NTP implementation is capable of maintaining the same time on two computers with an accuracy of around 1 ms - 30 ms despite the varying delays in internet propagation (see https://www.measurement.govt.nz/about-us/official-new-zealand-time/about-time/). | Two ticks Yes | One tick Somewhat Theoretically slightly less generation will be needed, so slight fall in wholesale electricity prices but non-particpants may incur costs from more inaccurate electronic clocks | Not applicable (Removing a non-market-based solution) | Not applicable (Removing a prescriptive solution) | Two ticks | 7
Issues 2, 3, 4 • An increasing amount of variable and intermittent resources, primarily in the form of wind and solar PV generation, is likely to cause greater voltage deviations, which are exacerbated by changing patterns of reactive power flows • Increasing amounts of inverter-based variable and intermittent resources will reduce the transmission network’s system strength thereby increasing the likelihood of network performance issues due to inverter-based resources disconnecting from the power system • Over time increasingly less generation capacity is expected to be subject to fault ride through obligations in the Code, as more generating stations export less than 30 MW to a network
36 | Place an obligation on asset owners (grid-connected parties, grid owners, and embedded generators) to support investigations into control interactions over the generating life of generating assets they own and/or which are connected to their asset(s) (in the case of network owners) | CQTG to clarify what is meant by investigations into control interactions
37 | Require the system operator to develop suitable technical requirements for fault ride through, which are consistent with and elaborate upon the fault ride through requirements in the Code | CQTG to advise what technical requirements, additional to what is specified in the Code, are needed at present
Issue 5 • There is some ambiguity around the applicability of harmonics standards and who manages harmonics (including the allocation of harmonics)
Issue 6 • Network operators have insufficient information on assets wanting to connect, or which are connected, to the power system to provide for the planning and operation of the power system in a safe, reliable, and economically efficient manner
38 | Require asset owners’ vendors to provide asset capability information that network operators require to meet their regulatory obligations | Feasible but expensive or has long implementation and/or moderate risk of unintended consequences (> 3 year code change, > 5 year asset change, > $50m). Would have to make vendors industry participants, which would require legislative change. Would be high risk of unintended consequences - with vendors asking why they have to be a participant in order for them to provide information that the asset owner could provide. Also the vendor's involvement with a network-connected asset typically is not for the life of the asset. | Not applicable | Not applicable | Not applicable | Not applicable | Not applicable | Not applicable | Not applicable
39 | Require asset owners (grid-connected parties, grid owners, and embedded generators) to provide asset capability information, encrypted if required by the asset owner or its vendor, that network owners require to optimise their network investments | Moderately feasible with low risk of unintended consequences (<2 years to change the Code, <3 years to change assets, <$20m implementation cost) | Two ticks Moderate The more accurate the data inputs a network owner has the more economically efficient are the network owner's investment options and decisions, because the network owner can more accurately model the behaviour of the power system when considering investment options | Two ticks Yes | One tick Somewhat Non marginal cost pricing and costs allocated in accordance with TPM (for grid owners) and DPM (for distributors) | Two crosses No | One cross No | Two ticks Depending on the threshold, this option may not be durable under a scenario of large uptake of small-scale distributed generation (eg, solar PV, batteries) because this SSDG would still not need to provide the information | 4
40 | Require asset owners’ vendors to provide asset capability information, encrypted if required by the vendor, that network owners require to optimise their network investments | Feasible but expensive or has long implementation and/or moderate risk of unintended consequences (> 3 year code change, > 5 year asset change, > $50m). Would have to make vendors industry participants, which would require legislative change. Would be high risk of unintended consequences - with vendors asking why they have to be a participant in order for them to provide information that the asset owner could provide. Also the vendor's involvement with a network-connected asset typically is not for the life of the asset. | Not applicable | Not applicable | Not applicable | Not applicable | Not applicable | Not applicable | Not applicable
41 | Establish a protocol for setting the frequency in islanded networks, including who the grid forming generator is | CQTG to provide further detail about this option
42 | Place an obligation on asset owners (grid-connected parties, grid owners, and embedded generators) to keep information provided to network operators up to date | This option does not appear necessary. Under clause 8.25(4) of the Code, each asset owner and each purchaser must provide information that complies with the technical codes or otherwise as the system operator reasonably requests, to assist the system operator in planning to comply, and complying, with its principal performance obligations and achieving the dispatch objective. Under clause 1B of Schedule 6.1 of the Code, a distributed generator that owns or operates distributed generation must apply to a distributor if it wishes to change the nameplate capacity or fuel type of the distributed generation connected to the distributor's distribution network. If a distributor wants to be advised of changes to other information provided to the distributor at the distributed generation connected, the distributor could specify this requirement in its connection and operation standards. | Not applicable | Not applicable | Not applicable | Not applicable | Not applicable | Not applicable | Not applicable
43 | Require asset owners (grid-connected parties, grid owners, and embedded generators) to provide network operators with energy dissipation information relating to their asset(s) riding through faults | CQTG to advise what information, additional to what is specified in the Code, is needed at present
Issue 7 • The Code is missing some terms that would help enable technologies, and contains some terms that appear to not be fit for the purpose of appropriately enabling technologies