## Summary of worked examples
Summary of worked examples
Scenario | Variant | Description | Location type | Posted charge | Flexi scheme | Customer-selected enhancement | Distributor-selected enhancement | Capacity cost allocation | Bespoke or project capacity cost | Active pioneer scheme | Local cost recovery scheme | Incremental transmission costs | Connection includes injection | Revenue life for reconciliation | Variants illustrate:
1. Small | 1a | Small urban residential connection with posted charge | urban | ü | û | û | û | û | û | û | û | û | û | 30 years | - use of posted charges - application of enhancement cost allocation, capacity costing, pioneer scheme calculations, and local cost recovery schemes - top-down revenue estimate.
| 1b | Small urban residential connection with two-phase connection | urban | ü | û | ü | û | û | û | û | û | û | û | 30 years
| 1c | Small urban residential connection with two-phase connection and upstream cost allocation | urban | ü | û | ü | û | ü | û | û | û | û | û | 30 years
| 1d | Upgrade of existing small urban residential connection to two-phase connection (with upstream cost allocation) | urban | û | û | û | û | ü | û | û | û | û | û | 30 years
| 1e | Small rural non-residential connection with upstream cost allocation | rural | û | û | û | û | ü | û | û | û | û | û | 15 years
| 1f | Small rural non-residential connection in location with active pioneer scheme | rural | û | û | û | û | ü | û | ü | û | û | û | 15 years
| 1g | Small rural non-residential connection in location with local cost recovery scheme | rural | û | û | û | û | ü | û | û | ü | û | û | 15 years
2. Remote mid-sized | 2a | Remote mid-sized connection with extension-like upgrade | remote | û | û | û | û | ü | bespoke | û | û | û | û | 15 years | - an extension-like upgrade - use of a bespoke capacity rate - bottom-up incremental revenue estimate - use of a minimum flexi scheme.
| 2b | Remote mid-sized flexi connection | remote | û | ü | û | û | ü | bespoke | û | û | û | û | 15 years
3. Large | 3a | Large connection at zone substation level with special pricing | urban | û | û | û | û | ü | û | û | û | û | û | 15 years | - reconciliation for a customer with special pricing - application of incremental transmission costs - the application of distribution connection pricing when there is both load and injection.
| 3b | Large connection at zone substation level with special pricing that involves GXP work (includes ITCs) | urban | û | û | û | û | ü | û | û | û | ü | û | 15 years
| 3c | Large connection at zone substation level with small injection (< 1 MVA) | urban | û | û | û | û | ü | û | û | û | û | ü | 15 years
| 3d | Large connection at zone substation level with mid-sized injection (~ 1.5 MVA) | urban | û | û | û | û | ü | û | û | û | û | ü | 15 years

## 1. small connection
Customer connection charge calculation for small connection variants (Scenario 1) | [6 empty] | key | input | linked | calculated | selection | set number
All $ inputs are real 2025
Explanatory notes
| Purpose | [8 empty] | Other comments
| The spreadsheet calculates the incremental cost and customer connection charge for the small connection (Scenario 1) variants in the Electricity Authority's distribution connnection pricing worked examples. It illustrates how a distributor allocates costs to the connection customer under the Authority's fast-tracked changes. Some data from this spreadsheet feeds into the 'Reconciliation model' spreadsheet. | [8 empty] | Numbers in this spreadsheet are indicative only. Distributors should determine their own numbers. Full descriptions of the variants are in the Electricity Authority's 'Worked Examples' report and are summarised in the 'Summary of worked examples' tab.
Layout of sheet
- This sheet is split into six sections, which are numbered 1-6 below. - Section 1 lists the variants in Scenario 1, section 2 presents the cost and charge build up for a selected variant, section 3 provides the incremental cost and connection charge for all variants, and sections 4-6 include the inputs and calculations for each of the components of the cost and charge build up (minimum scheme/minimum flexi scheme, customer-selected enhancement, and other costs and charges). - User should select the variant they're interested in (in the cell 'Sc1_variant' in section 1) to view the cost and charge build up for that variant in section 2. - The sheet relies on inputs from the '1f, Pioneer scheme', '1g. Local hist cost recovery', and 'Network costing zones' tabs, as well as the accompanying 'Reconciliation model' spreadsheet.
1. Variants
Variants shown in this sheet:
1a | Small urban residential connection with posted charge
1b | Small urban residential connection with two-phase connection
1c | Small urban residential connection with two-phase connection and upstream cost allocation
1d | Upgrade of existing small urban residential connection to two-phase connection (with upstream cost allocation)
1e | Small rural non-residential connection with upstream cost allocation
1f | Small rural non-residential connection in location with active pioneer scheme
1g | Small rural non-residential connection in location with local cost recovery scheme
| Variant for connection cost and charge summary |  | Variant 1d
2. Cost and charge build up for one variant
This section shows the build up of costs and charges for the variant selected in the 'Sc1_variant' cell above. First it shows the incremental cost and connection charge build up and then it shows other charges (eg, pioneer scheme charges and connection fees) that are not part of the connection charge.
Incremental cost and connection charge for Variant 1d
| Has the customer requested a flexi scheme? |  | No
| Is customer allocated upstream capacity costs? |  | Yes
| Minimum scheme/minimum flexi scheme (MS/MFS) | Unit | Cost | Charge | Description |  |  |  | Notes/assumptions
| MS/MFS- extension cost (EC) | $ | 1400 |  | Calculated cost for the minimum scheme or minimum flexi scheme (as applicable). |  |  |  | All of the Scenario 1 variants are based on the minimum scheme (not the minimum flexi scheme).
| MS/MFS - capacity (NCC) | $ | 1322.5 |  | Upstream capacity costs for the minimum scheme. |  |  |  | Are included in the cost regardless of whether the distributor allocates upstream capacity costs.
| MS/MFS (total) | $ | 2722.5 | 2722.5 |  |  |  |  | The new pricing requirements do not impose any direct constraints on the level of the MS/MFS charge. The distributor in Scenario 1 has decided to set a posted connection charge of $1,330 per connection for certain small residential connections. The requirements for this posted charge are meet by variants 1a-1c. For variant 1d, the distributor allocates 100% of the incremental cost. For variants 1e-1g, the distributor sets connection charges by crediting up to 65% of incremental revenue toward meeting incremental costs. Incremental revenue is calculated in the 'Reconciliation model' spreadsheet.
| Customer-selected enhancement (CSE) | Unit | Cost | Charge | Description |  |  |  | Notes/assumptions
| CSE - extension component | $ | 0 | 0 | Cost (and connection charge) for any customer-selected enhancement (excluding upstream capacity costs). |  |  |  | Full cost of CSE must be passed on to customer. Only applicable to variants 1b and 1c in Scenario 1.
| CSE - capacity component | $ | 0 | 0 | The incremental capacity cost of the CSE (ie, the capacity cost of any incremental demand over-and-above the demand under the minimum scheme or minimum flexi scheme). |  |  |  | If customer is allocated upstream capacity costs then full capacity component of CSE needs to be passed on to the customer. If customer is not allocated upstream capacity costs then charge for CSE - capacity component will be zero.
| CSE (total) | $ | 0 | 0
| Other cost and charge components | Unit | Cost | Charge | Description |  |  |  | Notes/assumptions
| Incremental transmission cost (ITC) | $ | 0 | 0 | Step change in transmission costs due to connection, including physical works to grid connections, and certain repricing events. Only applicable to certain large connections. |  |  |  | ITC not applicable for Scenario 1 variants.
| Localised historical cost recovery (LHCR) | $ | 0 | 0 | Total contribution paid by connecting party to localised historical cost recovery. |  |  |  | Only variant 1g has a LHCR.
| Operating cost loading (OCL) | $ | 0 |  | Addition to distributor's operating costs due to the new connection. Only relevant for large connections. |  |  |  | OCL not applicable for Scenario 1 variants.
| Incremental extension cost associated with generation | $ | 0 | 0 | The cost of any additional components required to support injection requirements at the connection. Does not include the cost of any components already included in the minimum scheme (or minimum flexi scheme) or any other enhancements. |  |  |  | Not applicable to Scenario 1 variants because they are load-only connections.
| Avoided cost of distribution (ACOD) | $ | 0 | 0 | Estimate of any identifiable avoided or avoidable costs of distribution associated with injection. Only applicable to connections with injection. |  |  |  | Not applicable to Scenario 1 variants because they are load-only connections.
| Total cost and charge |  | Cost | Charge | Description |  |  |  | Notes/assumptions
| Total incremental cost | $ | 2722.5
| Connection charge | $ |  | 2722.5
Other charges (not part of the connection charge) for Variant 1d
| Type of charge | Unit |  | Charge | Description |  |  |  | Notes/assumptions
| Total pioneer scheme charge | $ |  | 0 | Total contribution paid by connecting party to pioneer scheme (if applicable). |  |  |  | Only applicable to variant 1f.
| Connection fees | $ |  | 220 | Fees based on the cost of administering the connection process.
3. Incremental cost and connection charge for all Scenario 1 variants
| Incremental cost and connection charge | Unit | Variant 1a | Variant 1b | Variant 1c | Variant 1d | Variant 1e | Variant 1f | Variant 1g | Description |  |  | Notes/assumptions
| Incremental cost (IC) | $ | 5782.5 | 8105 | 8105 | 2722.5 | 17065 | 17065 | 37065 | Equal to the sum of the MS/MFS extension cost (EC), MS/MFS capacity cost (NCC), CSE extension cost, CSE capacity cost, ITC (if applicable), LHCR (if applicable), OCL (if applicable), and incremental extension cost associated with generation (if applicable) less ACOD (if applicable).
| Connection charge (CC) | $ | 1330 | 2330 | 3652.5 | 2722.5 | 11476 | 11476 | 31476 | Equal to the sum of the MS/MFS charge (posted or otherwise), the CSE cost (excluding the capacity cost if capacity costs are not allocated), up-front charge for ITC (if applicable), the LHCR (if applicable), and any charge for the incremental extension cost associated with generation (if applicable), less any reduction in charge due to ACOD (if applicable).
| Upstream capacity cost allocation |  | Variant 1a | Variant 1b | Variant 1c | Variant 1d | Variant 1e | Variant 1f | Variant 1g | Notes/assumptions
| Is the customer allocated upstream capacity costs? |  | No | No | Yes | Yes | Yes | Yes | Yes | If yes, must use posted capacity rates to determine capacity cost (unless criteria for using a modified capacity rate or a share of actual project costs is met).
4. Minimum scheme/minimum flexi scheme calculations for all Scenario 1 variants
Calculation of minimum scheme/minimum flexi scheme cost
Minimum scheme/minimum flexi scheme extension cost (EC) calculation
|  |  | Variant 1a | Variant 1b | Variant 1c | Variant 1d | Variant 1e | Variant 1f | Variant 1g | Notes/assumptions
| Has the customer requested a flexi scheme? |  | No | No | No | No | No | No | No | Minimum flexi scheme only needs to be costed if customer requests minimum flexi scheme. If minimum flexi scheme is not requested then minimum flexi scheme cost components are shaded dark grey (as not applicable).
| Components of minimum scheme cost | Unit | Variant 1a | Variant 1b | Variant 1c | Variant 1d | Variant 1e | Variant 1f | Variant 1g | Notes/assumptions
| ~400 V LV Overhead line | $ | 600 | 600 | 600 | 300 | 600 | 600 | 600 | $15/m - 95mm2 Al Fluorine AAAC (or similar). All lengths assumed to be 20 m per phase or neutral.
| ~400 V Pole / Cross Arm | $ |  |  |  |  | 13200 | 13200 | 13200 | The cost is inclusive of a fully dressed pole and cable termination equipment.
| ~400 V Single Phase Pole Fuse | $ | 100 | 100 | 100 | 100 | 100 | 100 | 100 | Single Phase 63 A Fuse.
| Install Costs | $ | 1200 | 1200 | 1200 | 1000 | 2085 | 2085 | 2085 | Variant 1a to 1c equals 3 people for 4 hours at $100/hour. Variant 1c is for the install of a second phase to an existing single phase connection - have assumed there would be some savings in install time (as there is an existing connection). Variant 1e to 1g assumes install costs are 15% of other components.
| Total minimum scheme cost | $ | 1900 | 1900 | 1900 | 1400 | 15985 | 15985 | 15985
| Components of minimum flexi scheme cost | Unit | Variant 1a | Variant 1b | Variant 1c | Variant 1d | Variant 1e | Variant 1f | Variant 1g | Notes/assumptions
$
$
$
$
| Total minimum flexi scheme cost | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum scheme/minimum flexi scheme capacity cost (NCC) calculation
|  | Unit | Variant 1a | Variant 1b | Variant 1c | Variant 1d | Variant 1e | Variant 1f | Variant 1g | Notes/assumptions
| Network costing zone | zone | Urban | Urban | Urban | Urban | Rural A | Rural A | Rural A | Distributor may segment their network into network costing zones.
| Capacity cost | Unit | Variant 1a | Variant 1b | Variant 1c | Variant 1d | Variant 1e | Variant 1f | Variant 1g | Notes/assumptions
| Low voltage mains (LV) | $/kVA | 240 | 240 | 240 | 240 | 0 | 0 | 0 | Capacity costs (by network tier) are pulled from the 'Network costing zones' tab. A distributor can set a posted capacity rate to zero (for any tier) where there is no foreseeable upgrade needed.
| Distribution substation (DS) | $/kVA | 600 | 600 | 600 | 600 | 0 | 0 | 0
| High voltage feeder (HVF) | $/kVA | 85 | 85 | 85 | 85 | 85 | 85 | 85
| Zone substation (ZS) | $/kVA | 380 | 380 | 380 | 380 | 380 | 380 | 380
| Sub-transmission line (STL) | $/kVA | 140 | 140 | 140 | 140 | 100 | 100 | 100
| Capacity demand - minimum scheme/minimum flexi scheme | Unit | Variant 1a | Variant 1b | Variant 1c | Variant 1d | Variant 1e | Variant 1f | Variant 1g | Notes/assumptions
| Low voltage mains (LV) | kVA | 5 | 5 | 5 | 3 | 4 | 4 | 4 | Demand assumptions allow for diversity. Demand for variant 1d is just the incremental demand (for the second phase) so is equal to the incremental demand for the CSE in variants 1c and 1d.
| Distribution substation (DS) | kVA | 2.5 | 2.5 | 2.5 | 0.5 | 4 | 4 | 4
| High voltage feeder (HVF) | kVA | 2.5 | 2.5 | 2.5 | 0.5 | 2 | 2 | 2
| Zone substation (ZS) | kVA | 2 | 2 | 2 | 0.5 | 2 | 2 | 2
| Sub-transmission line (STL) | kVA | 1.5 | 1.5 | 1.5 | 0.5 | 1.5 | 1.5 | 1.5
| Calculation of upstream capacity cost - minimum scheme/minimum flexi scheme | Unit | Variant 1a | Variant 1b | Variant 1c | Variant 1d | Variant 1e | Variant 1f | Variant 1g | Notes/assumptions
| Low voltage mains (LV) | $ | 1200 | 1200 | 1200 | 720 | 0 | 0 | 0 | The capacity cost for a tier (if the tier is required by the connection) is the posted capacity rate multiplied by the capacity demand for the relevant tier. Estimated capacity upgrade costs or estimated capacity rates can be used when specific criteria are met, but the variants in Scenario 1 do not meet these criteria (see variant 2a for an example of these criteria applying).
| Distribution substation (DS) | $ | 1500 | 1500 | 1500 | 300 | 0 | 0 | 0
| High voltage feeder (HVF) | $ | 212.5 | 212.5 | 212.5 | 42.5 | 170 | 170 | 170
| Zone substation (ZS) | $ | 760 | 760 | 760 | 190 | 760 | 760 | 760
| Sub-transmission line (STL) | $ | 210 | 210 | 210 | 70 | 150 | 150 | 150
| Total upstream capacity cost (minimum scheme/minimum flexi scheme only) | $ | 3882.5 | 3882.5 | 3882.5 | 1322.5 | 1080 | 1080 | 1080
Minimum scheme/minimum flexi scheme charge
| Minimum scheme/minimum flexi scheme charge | Unit | Variant 1a | Variant 1b | Variant 1c | Variant 1d | Variant 1e | Variant 1f | Variant 1g | Notes/assumptions
| What is the connection charge for the minimum scheme/minimum flexi scheme? | $ | 1330 | 1330 | 1330 | 2722.5 | 11476 | 11476 | 11476 | Either applied to minimum scheme or minimum flexi scheme (whichever is relevant). Variants 1a-1c meet the distributor's requirements for their residential posted charge of $1,330. For variant 1d, the distributor's connection pricing methodology sets out that they will allocate the full cost (including network capacity cost) for connection of a second phase. For variants 1e-1g, the distributor sets connection charges by crediting up to 65% of incremental revenue toward meeting incremental costs. Incremental revenue is calculated in the 'Reconciliation model' spreadsheet.
5. Customer-selected enhancement calculations for all Scenario 1 variants
Customer-selected enhancement extension component
| Components of CSE extension cost | Unit | Variant 1a | Variant 1b | Variant 1c | Variant 1d | Variant 1e | Variant 1f | Variant 1g | Notes/assumptions
| ~400 V LV Overhead line | $ |  | 300 | 300 |  |  |  |  | $15/m - 95mm2 Al Fluorine AAAC (or similar). All lengths assumed to be 20 m per phase or neutral
| ~400 V 2-Phase Pole Fuse | $ |  | 100 | 100 |  |  |  |  | 63 A, 2ph fuse
| Install Costs | $ |  | 600 | 600 |  |  |  |  | Have assumed 3 people for 2 hours each (at $100 per hour) to install a second phase (in addition to the time required to install the first phase).
| Total CSE extension cost | $ | 0 | 1000 | 1000 | 0 | 0 | 0 | 0
Customer-selected enhancement capacity cost component
|  | Unit | Variant 1a | Variant 1b | Variant 1c | Variant 1d | Variant 1e | Variant 1f | Variant 1g | Notes/assumptions
| Network costing zone | zone | Urban | Urban | Urban | Urban | Rural A | Rural A | Rural A | Same network costing zones as used for minimum scheme/minimum flexi scheme above.
| Capacity cost | Unit | Variant 1a | Variant 1b | Variant 1c | Variant 1d | Variant 1e | Variant 1f | Variant 1g | Notes/assumptions
| Low voltage mains (LV) | $/kVA | 240 | 240 | 240 | 240 | 0 | 0 | 0 | Capacity costs (by network tier) are pulled from the 'Network costing zones' tab. A distributor can set a posted capacity rate to zero (for any tier) where there is no foreseeable upgrade needed.
| Distribution substation (DS) | $/kVA | 600 | 600 | 600 | 600 | 0 | 0 | 0
| High voltage feeder (HVF) | $/kVA | 85 | 85 | 85 | 85 | 85 | 85 | 85
| Zone substation (ZS) | $/kVA | 380 | 380 | 380 | 380 | 380 | 380 | 380
| Sub-transmission line (STL) | $/kVA | 140 | 140 | 140 | 140 | 100 | 100 | 100
| Capacity demand - customer-selected enhancement | Unit | Variant 1a | Variant 1b | Variant 1c | Variant 1d | Variant 1e | Variant 1f | Variant 1g | Notes/assumptions
| Low voltage mains (LV) | kVA |  | 3 | 3 |  |  |  |  | Demand assumptions allow for diversity. This is the incremental demand for the customer-selected enhancement (ie, over-and-above the demand under the minimum scheme or minimum flexi scheme).
| Distribution substation (DS) | kVA |  | 0.5 | 0.5
| High voltage feeder (HVF) | kVA |  | 0.5 | 0.5
| Zone substation (ZS) | kVA |  | 0.5 | 0.5
| Sub-transmission line (STL) | kVA |  | 0.5 | 0.5
| Calculation of upstream capacity cost - CSE | Unit | Variant 1a | Variant 1b | Variant 1c | Variant 1d | Variant 1e | Variant 1f | Variant 1g | Notes/assumptions
| Low voltage mains (LV) | $ | 0 | 720 | 720 | 0 | 0 | 0 | 0 | The capacity cost allocation for a tier (if the tier is required by the connection) is the posted capacity rate multiplied by the incremental capacity demand for the relevant tier for the customer-selected enhancment.
| Distribution substation (DS) | $ | 0 | 300 | 300 | 0 | 0 | 0 | 0
| High voltage feeder (HVF) | $ | 0 | 42.5 | 42.5 | 0 | 0 | 0 | 0
| Zone substation (ZS) | $ | 0 | 190 | 190 | 0 | 0 | 0 | 0
| Sub-transmission line (STL) | $ | 0 | 70 | 70 | 0 | 0 | 0 | 0
| Total upstream capacity cost - CSE | $ | 0 | 1322.5 | 1322.5 | 0 | 0 | 0 | 0
6. Other cost and charge calculations for all Scenario 1 variants
Localised historical cost recovery (LHCR)
| Type of charge | Unit | Variant 1a | Variant 1b | Variant 1c | Variant 1d | Variant 1e | Variant 1f | Variant 1g | Description |  |  | Notes/assumptions
| Localised historical cost recovery (LHCR) | $ | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | Total contribution paid by connecting party to localised historical cost recovery. |  |  | Calculated in '1g. Local hist cost recovery' tab for variant 1g (the only variant with a localised historical cost recovery scheme).
Pioneer scheme charge
Note: is not part of the connection charge
| Type of charge | Unit | Variant 1a | Variant 1b | Variant 1c | Variant 1d | Variant 1e | Variant 1f | Variant 1g | Description |  |  | Notes/assumptions
| Total pioneer scheme charge | $ | 0 | 0 | 0 | 0 | 0 | 7500 | 0 | Total contribution paid by connecting party to pioneer scheme. |  |  | Calculated in '1f. Pioneer scheme' tab for variant 1f (the only variant with an active pioneer scheme).
Connection fees
Note: is not part of the connection charge and excludes any adminstration fee for a pioneer scheme
| Type of fee | Unit | Variant 1a | Variant 1b | Variant 1c | Variant 1d | Variant 1e | Variant 1f | Variant 1g | Description |  |  | Notes/assumptions
| Application processing | $ | 140 | 140 | 140 | 140 | 140 | 140 | 140 | Application processing fee based on the costs of administering the connection process. |  |  | We have based on fees in Part 6 of the Code, but this is not a requirement.
| Technical observation | $ | 80 | 80 | 80 | 80 | 80 | 80 | 80 | Technical observation fee based on the csots of adminisering the connection process. |  |  | We have based on fees in Part 6 of the Code, but this is not a requirement.
| Total fees | $ | 220 | 220 | 220 | 220 | 220 | 220 | 220

## 2. remote mid-sized connection
Customer connection charge calculation for remote mid-sized connection variants (Scenario 2) | [5 empty] | key | input | linked | calculated | selection | set number
All $ inputs are real 2025
Explanatory notes
| Purpose | [5 empty] | Other comments
| The spreadsheet calculates the incremental cost and customer connection charge for the remote mid-sized connection (Scenario 2) variants in the Electricity Authority's distribution connnection pricing worked examples. It illustrates how a distributor allocates costs to the connection customer under the Authority's fast-tracked changes. Some data from this spreadsheet feeds into the 'Reconciliation model' spreadsheet. | [5 empty] | Numbers in this spreadsheet are indicative only. Distributors should determine their own numbers. Full descriptions of the variants are in the Electricity Authority's 'Worked Examples' report and are summarised in the 'Summary of worked examples' tab.
Layout of sheet
- This sheet is split into six sections, which are numbered 1-6 below. - Section 1 lists the variants in Scenario 2, section 2 presents the cost and charge build up for a selected variant, section 3 provides the incremental cost and connection charge for all variants, and sections 4-6 include the inputs and calculations for each of the components of the cost and charge build up (minimum scheme/minimum flexi scheme, customer-selected enhancement, and other costs and charges). - User should select the variant they're interested in (in the cell 'Sc2_variant' in section 1) to view the cost and charge build up for that variant in section 2. - The sheet relies on inputs from the 'Network costing zones' tab, as well as the accompanying 'Reconciliation model' spreadsheet.
1. Variants
Variants shown in this sheet:
2a | Remote mid-sized connection with extension-like upgrade
2b | Remote mid-sized flexi connection
| Variant for connection cost and charge summary |  | Variant 2a
2. Cost and charge build up for one variant
This section shows the build up of costs and charges for the variant selected in the 'Sc2_variant' cell above. First it shows the incremental cost and connection charge build up and then it shows other charges (eg, pioneer scheme charges and connection fees) that are not part of the connection charge.
Incremental cost and connection charge for Variant 2a
| Has the customer requested a flexi scheme? |  | No
| Is customer allocated upstream capacity costs? |  | Yes
| Minimum scheme/minimum flexi scheme (MS/MFS) | Unit | Cost | Charge | Description |  |  | Notes/assumptions
| MS/MFS- extension cost (EC) | $ | 145200 |  | Calculated cost for the minimum scheme or minimum flexi scheme (as applicable). |  |  | Variant 2a is based on the minimum scheme, while variant 2b is based on the minimum flexi scheme.
| MS/MFS - capacity (NCC) | $ | 51700 |  | Upstream capacity costs for the minimum scheme. |  |  | Are included in the cost regardless of whether the distributor allocates upstream capacity costs.
| MS/MFS (total) | $ | 196900 | 164170 |  |  |  | The new pricing requirements do not impose any direct constraints on the level of the MS/MFS charge. For Scenario 2 we have assumed that the distributor's connection pricing methodology puts up to 18% of incremental revenue toward covering incremental costs. Incremental revenue is about $184k for variants 2a and 2b, so the connection charge can be up to $32,730 lower than the incremental cost. We have assumed the connection charge is $32,730 lower than the incremental cost for varaints 2a and 2b.
| Customer-selected enhancement (CSE) | Unit | Cost | Charge | Description |  |  | Notes/assumptions
| CSE - extension component | $ | 0 | 0 | Cost (and connection charge) for any customer-selected enhancement (excluding upstream capacity costs). |  |  | Full cost of CSE must be passed on to customer. Not applicable to Scenario 2 variants.
| CSE - capacity component | $ | 0 | 0 | The incremental capacity cost of the CSE (ie, the capacity cost of any incremental demand over-and-above the demand under the minimum scheme or minimum flexi scheme). |  |  | If customer is allocated upstream capacity costs then full capacity component of CSE needs to be passed on to the customer. If customer is not allocated upstream capacity costs then charge for CSE - capacity component will be zero.
| CSE (total) | $ | 0 | 0
| Other cost and charge components | Unit | Cost | Charge | Description |  |  | Notes/assumptions
| Incremental transmission cost (ITC) | $ | 0 |  | Step change in transmission costs due to connection, including physical works to grid connections, and certain repricing events. Only applicable to certain large connections. |  |  | ITC not applicable to Scenario 2 variants.
| Localised historical cost recovery (LHCR) | $ | 0 | 0 | Total contribution paid by connecting party to localised historical cost recovery. |  |  | LHRC not applicable to Scenario 2 variants.
| Operating cost loading (OCL) | $ | 0 |  | Addition to distributor's operating costs due to the new connection. Only relevant for large connections. |  |  | OCL not applicable to Scenario 2 variants.
| Incremental extension cost associated with generation | $ | 0 | 0 | The cost of any additional components required to support injection requirements at the connection.Does not include the cost of any components already included in the minimum scheme (or minimum flexi scheme) or any other enhancements. |  |  | Not applicable to Scenario 2 variants because they are load-only connections.
| Avoided cost of distribution (ACOD) | $ | 0 | 0 | Estimate of any identifiable avoided or avoidable costs of distribution associated with injection. Only applicable to connections with injection. |  |  | Not applicable to Scenario 2 variants because they are load-only connections.
| Total cost and charge |  | Cost | Charge | Description |  |  | Notes/assumptions
| Total incremental cost | $ | 196900
| Connection charge | $ |  | 164170
Other charges (not part of the connection charge) for Variant 2a
| Type of charge | Unit |  | Charge | Description |  |  | Notes/assumptions
| Total pioneer scheme charge | $ |  | 0 | Total contribution paid by connecting party to pioneer scheme (if applicable). |  |  | Not applicable to Scenario 2 variants.
| Connection fees | $ |  | 950 | Fees based on the cost of administering the connection process.
3. Incremental cost and connection charge for all Scenario 2 variants
| Incremental cost and connection charge | Unit | Variant 2a | Variant 2b | Description |  |  | Notes/assumptions
| Incremental cost (IC) | $ | 196900 | 58310 | Equal to the sum of the MS/MFS extension cost (EC), MS/MFS capacity cost (NCC), CSE extension cost, CSE capacity cost, ITC (if applicable), LHCR (if applicable), OCL (if applicable), and incremental extension cost associated with generation (if applicable) less ACOD (if applicable).
| Connection charge (CC) | $ | 164170 | 25580 | Equal to the sum of the MS/MFS charge (posted or otherwise), the CSE cost (excluding the capacity cost if capacity costs are not allocated), up-front charge for ITC (if applicable), the LHCR (if applicable), and any charge for the incremental extension cost associated with generation (if applicable), less any reduction in charge due to ACOD (if applicable).
| Upstream capacity cost allocation |  | Variant 2a | Variant 2b | Notes/assumptions
| Is the customer allocated upstream capacity costs? |  | Yes | Yes | If yes, must use posted capacity rates to determine capacity cost (unless criteria for using a modified capacity rate or a share of actual project costs is met).
4. Minimum scheme/minimum flexi scheme calculations for all Scenario 2 variants
Calculation of minimum scheme/minimum flexi scheme cost
Minimum scheme/minimum flexi scheme extension cost (EC) calculation
|  |  | Variant 2a | Variant 2b | Notes/assumptions
| Has the customer requested a flexi scheme? |  | No | Yes | Minimum flexi scheme only needs to be costed if customer requests minimum flexi scheme. If minimum flexi scheme is not requested then minimum flexi scheme cost components are shaded dark grey (as not applicable).
| Components of minimum scheme cost | Unit | Variant 2a | Variant 2b | Notes/assumptions
| Ground Mounted Dist Transformer | $ | 100000 |  | Dyn11 - 11kV/415-240V - Ground Mt 300kVA 3Ph (inc install)
| ~400 V LV Overhead line | $ | 1200 |  | $15/m - 95mm2 Al Fluorine AAAC (or similar) (inc install). Assumed 20 m * 4
| 400 V Switchboard | $ | 44000 |  | 400 V Switchboard, assumed to be the price of a Service Pillar
| Total minimum scheme cost | $ | 145200 | 0
| Components of minimum flexi scheme cost | Unit | Variant 2a | Variant 2b | Notes/assumptions
| 1x 11 kV Comms Panel | $ |  | 20000 | Price including fibre connection between the two sites.
| Pole Mounted Dist Transformer |  |  |  | Not required
| ~400 V LV Overhead line | $ |  | 1200 | $15/m - 95mm2 Al ABC / Fluorine AAAC (or similar) (inc install). Assumed 20 m * 4
| 400 V Switchboard | $ |  |  | Not required
| Labour Costs | $ |  | 2000
| Total minimum flexi scheme cost | $ | 0 | 23200
Minimum scheme/minimum flexi scheme capacity cost (NCC) calculation
|  | Unit | Variant 2a | Variant 2b | Notes/assumptions
| Network costing zone | zone | Rural B | Rural B | Distributor may segment their network into network costing zones.
| Capacity cost | Unit | Variant 2a | Variant 2b | Notes/assumptions
| Low voltage mains (LV) | $/kVA | 170 | 170 | Capacity costs (by network tier) are pulled from the 'Network costing zones' tab. A distributor can set a posted capacity rate to zero (for any tier) where there is no foreseeable upgrade needed.
| Distribution substation (DS) | $/kVA | 530 | 530
| High voltage feeder (HVF) | $/kVA | 85 | 85
| Zone substation (ZS) | $/kVA | 380 | 380
| Sub-transmission line (STL) | $/kVA | 100 | 100
| Capacity demand - minimum scheme/minimum flexi scheme | Unit | Variant 2a | Variant 2b | Notes/assumptions
| Low voltage mains (LV) | kVA | 0 | 0 | Demand assumptions allow for diversity.
| Distribution substation (DS) | kVA | 0 | 50
| High voltage feeder (HVF) | kVA | 100 | 50
| Zone substation (ZS) | kVA | 80 | 2
| Sub-transmission line (STL) | kVA | 60 | 2
| Can estimated capacity upgrade costs be used |  | Variant | Variant | Notes/assumptions
Is the demand increment from the project more than 80% of the nominal capacity increment for:
| the high voltage feeder (HVF) tier? |  | No | No | If yes, can use estimated capacity upgrade costs for the HVF tier instead of the posted capacity rate.
| the zone substation (ZS) tier? |  | No | No | If yes, can use estimated capacity upgrade costs for the ZS tier instead of the posted capacity rate.
| the sub-transmission line (STL) tier? |  | No | No | If yes, can use estimated capacity upgrade costs for the STL tier instead of the posted capacity rate.
If yes, what is the estimated capacity upgrade costs?
| the high voltage feeder (HVF) tier? | $
| the zone substation (ZS) tier? | $
| the sub-transmission line (STL) tier? | $
| Can modified capacity rates be used |  | Variant | Variant | Notes/assumptions
Is the cost per unit of the upgrade project estimated to be more than 150%, or lower than 80%, of the applicable posted capacity rate for:
| the high voltage feeder (HVF) tier? |  | Yes | Yes | N/A if estimated capacity upgrade costs can be used (see above) or if there is no capacity demand at that tier. If yes, can use estimated capacity rate rather than posted capacity rate.
| the zone substation (ZS) tier? |  | No | No | N/A if estimated capacity upgrade costs can be used (see above) or if there is no capacity demand at that tier. If yes, can use estimated capacity rate rather than posted capacity rate.
| the sub-transmission line (STL) tier? |  | No | No | N/A if estimated capacity upgrade costs can be used (see above) or if there is no capacity demand at that tier. If yes, can use estimated capacity rate rather than posted capacity rate.
If yes, what is the estimated cost per unit relative to the posted rate for:
| the high voltage feeder (HVF) tier? | % | 180% | 180% | Needs to be greater than 150% (if cost per unit is higher than average) or less than 80% (if cost per unit is lower than average). Cell will be dark grey if not applicable (when the cost per unit of the upgrade project is between 80% and 150% of the applicable posted capacity rate OR if estimated capacity upgrade costs can be used).
| the zone substation (ZS) tier? | %
| the sub-transmission line (STL) tier? | %
| Calculation of upstream capacity cost - minimum scheme/minimum flexi scheme | Unit | Variant 2a | Variant 2b | Notes/assumptions
| Low voltage mains (LV) | $ | 0 | 0 | The capacity cost for a tier (if the tier is required by the connection) is the posted capacity rate multiplied by the capacity demand for the relevant tier. Estimated capacity upgrade costs or estimated capacity rates can be used when specific criteria are met (see variant 2a for an example of these criteria applying).
| Distribution substation (DS) | $ | 0 | 26500
| High voltage feeder (HVF) | $ | 15300 | 7650
| Zone substation (ZS) | $ | 30400 | 760
| Sub-transmission line (STL) | $ | 6000 | 200
| Total upstream capacity cost (minimum scheme/minimum flexi scheme only) | $ | 51700 | 35110
Minimum scheme/minimum flexi scheme charge
| Minimum scheme/minimum flexi scheme charge | Unit | Variant 2a | Variant 2b | Notes/assumptions
| What is the connection charge for the minimum scheme/minimum flexi scheme? | $ | 164170 | 25580 | Either applied to minimum scheme or minimum flexi scheme (whichever is relevant). For both variants the distributor sets connection charges by crediting up to 15% of incremental revenue toward meeting incremental costs.
5. Customer-selected enhancement calculations for all Scenario 2 variants
Customer-selected enhancement extension component
| Components of CSE extension cost | Unit | Variant 2a | Variant 2b | Notes/assumptions
$
$
| Total CSE extension cost | $ | 0 | 0
Customer-selected enhancement capacity cost component
|  | Unit | Variant 2a | Variant 2b | Notes/assumptions
| Network costing zone | zone | Rural B | Rural B | Same network costing zones as used for minimum scheme/minimum flexi scheme above.
| Capacity cost | Unit | Variant 2a | Variant 2b | Notes/assumptions
| Low voltage mains (LV) | $/kVA | 170 | 170 | Capacity costs (by network tier) are pulled from the 'Network costing zones' tab. A distributor can set a posted capacity rate to zero (for any tier) where there is no foreseeable upgrade needed.
| Distribution substation (DS) | $/kVA | 530 | 530
| High voltage feeder (HVF) | $/kVA | 85 | 85
| Zone substation (ZS) | $/kVA | 380 | 380
| Sub-transmission line (STL) | $/kVA | 100 | 100
| Capacity demand - customer-selected enhancement | Unit | Variant 2a | Variant 2b | Notes/assumptions
| Low voltage mains (LV) | kVA |  |  | Demand assumptions allow for diversity. This is the incremental demand for the customer-selected enhancement (ie, over-and-above the demand under the minimum scheme or minimum flexi scheme).
| Distribution substation (DS) | kVA
| High voltage feeder (HVF) | kVA
| Zone substation (ZS) | kVA
| Sub-transmission line (STL) | kVA
| Calculation of upstream capacity cost - CSE | Unit | Variant 2a | Variant 2b | Notes/assumptions
| Low voltage mains (LV) | $ | 0 | 0 | The capacity cost allocation for a tier (if the tier is required by the connection) is the posted capacity rate multiplied by the incremental capacity demand for the relevant tier for the customer-selected enhancment.
| Distribution substation (DS) | $ | 0 | 0
| High voltage feeder (HVF) | $ | 0 | 0
| Zone substation (ZS) | $ | 0 | 0
| Sub-transmission line (STL) | $ | 0 | 0
| Total upstream capacity cost - CSE | $ | 0 | 0
6. Other cost and charge calculations for all Scenario 2 variants
Localised historical cost recovery (LHCR)
| Type of charge | Unit | Variant 2a | Variant 2b | Description |  |  | Notes/assumptions
| Localised historical cost recovery (LHCR) | $ | 0 | 0 | Total contribution paid by connecting party to localised historical cost recovery. |  |  | Not applicable to Scenario 2 variants.
Pioneer scheme charge
Note: is not part of the connection charge
| Type of charge | Unit | Variant 2a | Variant 2b | Description |  |  | Notes/assumptions
| Total pioneer scheme charge | $ | 0 | 0 | Total contribution paid by connecting party to pioneer scheme. |  |  | Not applicable to Scenario 2 variants.
Connection fees
Note: is not part of the connection charge and excludes any adminstration fee for a pioneer scheme
| Type of fee | Unit | Variant 2a | Variant 2b | Description |  |  | Notes/assumptions
| Application processing | $ | 770 | 770 | Application processing fee based on the costs of administering the connection process. |  |  | We have based on fees in Part 6 of the Code, but this is not a requirement.
| Technical observation | $ | 180 | 180 | Technical observation fee based on the csots of adminisering the connection process. |  |  | We have based on fees in Part 6 of the Code, but this is not a requirement.
| Total fees | $ | 950 | 950

## 3. large connection
Customer connection charge calculation for large connection variants (Scenario 3) | [6 empty] | key | input | linked | calculated | selection | set number
All $ inputs are real 2025
Explanatory notes
| Purpose | [6 empty] | Other comments
| The spreadsheet calculates the incremental cost and customer connection charge for the large connection (Scenario 3) variants in the Electricity Authority's distribution connnection pricing worked examples. It illustrates how a distributor allocates costs to the connection customer under the Authority's fast-tracked changes. Some data from this spreadsheet feeds into the 'Reconciliation model' spreadsheet. | [6 empty] | Numbers in this spreadsheet are indicative only. Distributors should determine their own numbers. Full descriptions of the variants are in the Electricity Authority's 'Worked Examples' report and are summarised in the 'Summary of worked examples' tab.
Layout of sheet
- This sheet is split into six sections, which are numbered 1-6 below. - Section 1 lists the variants in Scenario 3, section 2 presents the cost and charge build up for a selected variant, section 3 provides the incremental cost and connection charge for all variants, and sections 4-6 include the inputs and calculations for each of the components of the cost and charge build up (minimum scheme/minimum flexi scheme, customer-selected enhancement, and other costs and charges). - User should select the variant they're interested in (in the cell 'Sc3_variant' in section 1) to view the cost and charge build up for that variant in section 2. - The sheet relies on inputs from the 'Network costing zones' tab, as well as the accompanying 'Reconciliation model' spreadsheet.
1. Variants
Variants shown in this sheet:
3a | Large connection at zone substation level with special pricing
3b | Large connection at zone substation level with special pricing that involves GXP work (includes incremental transmission costs)
3c | Large connection at zone substation level with small injection (< 1 MVA)
3d | Large connection at zone substation level with mid-sized injection (~ 1.5 MVA)
| Variant for connection cost and charge summary |  | Variant 3a
2. Cost and charge build up for one variant
This section shows the build up of costs and charges for the variant selected in the 'Sc3_variant' cell above. First it shows the incremental cost and connection charge build up and then it shows other charges (eg, pioneer scheme charges and connection fees) that are not part of the connection charge.
Incremental cost and connection charge for Variant 3a
| Has the customer requested a flexi scheme? |  | No
| Is customer allocated upstream capacity costs? |  | Yes
| Minimum scheme/minimum flexi scheme (MS/MFS) | Unit | Cost | Charge | Description |  |  |  | Notes/assumptions
| MS/MFS- extension cost (EC) | $ | 204000 |  | Calculated cost for the minimum scheme or minimum flexi scheme (as applicable). |  |  |  | All of the Scenario 3 variants are based on the minimum scheme (not the minimum flexi scheme).
| MS/MFS - capacity (NCC) | $ | 1940000 |  | Upstream capacity costs for the minimum scheme. |  |  |  | Are included in the cost regardless of whether the distributor allocates upstream capacity costs.
| MS/MFS (total) | $ | 2144000 | 2144000 |  |  |  |  | The new pricing requirements do not impose any direct constraints on the level of the MS/MFS charge. For Scenario 3 variants we have assumed that the distributor and connection applicant agree to recover all up-front costs through up-front connection charges.
| Customer-selected enhancement (CSE) | Unit | Cost | Charge | Description |  |  |  | Notes/assumptions
| CSE - extension component | $ | 0 | 0 | Cost (and connection charge) for any customer-selected enhancement (excluding upstream capacity costs). |  |  |  | Full cost of CSE must be passed on to customer. Not applicable to Scenario 3 variants.
| CSE - capacity component | $ | 0 | 0 | The incremental capacity cost of the CSE (ie, the capacity cost of any incremental demand over-and-above the demand under the minimum scheme or minimum flexi scheme). |  |  |  | If customer is allocated upstream capacity costs then full capacity component of CSE needs to be passed on to the customer. If customer is not allocated upstream capacity costs then charge for CSE - capacity component will be zero.
| CSE (total) | $ | 0 | 0
| Other cost and charge components | Unit | Cost | Charge | Description |  |  |  | Notes/assumptions
| Incremental transmission cost (ITC) | $ | 0 | 0 | Step change in transmission costs due to connection, including physical works to grid connections, and certain repricing events. Only applicable to certain large connections. |  |  |  | ITC only applicable to variant 3b. We have assumed that the (present value of) the cost of GXP works ($239k for variant 3b) is recovered through the connection charge and (the present value) of pricing-related ITC (the remainder of the ITC) is recovered through annual charges. See '3b. ITC calcs' tab for ITC calculations.
| Localised historical cost recovery (LHCR) | $ | 0 | 0 | Total contribution paid by connecting party to localised historical cost recovery. |  |  |  | LHRC not applicable to Scenario 3 variants.
| Operating cost loading (OCL) | $ | 111120.8316 |  | Addition to distributor's operating costs due to the new connection. Only relevant for large connections. |  |  |  | For Scenario 3 variants, we have assumed that the distributor estimates an operating cost equivalent to 5% of the up-front extension asset cost each year. Sums the NPV of annual opex for the connection for all years in the revenue life. OCL is calculated in the 'Reconciliation model' spreadsheet.
| Incremental extension cost associated with generation | $ | 0 | 0 | The cost of any additional components required to support injection requirements at the connection.Does not include the cost of any components already included in the minimum scheme (or minimum flexi scheme) or any other enhancements. |  |  |  | Only applicable to variants 3c and 3d (because 3a and 3b do not have injection). However, estimated to be zero for variant 3c because no additional components are required to support injection.
| Avoided cost of distribution (ACOD) | $ | 0 | 0 | Estimate of any identifiable avoided or avoidable costs of distribution associated with injection. Only applicable to connections with injection. |  |  |  | Only applicable to variants 3c and 3d (because 3a and 3b do not have injection). However, estimated to be zero for variant 3d. Has been estimated using capacity costing rates, but this is not a required approach.
| Total cost and charge |  | Cost | Charge | Description |  |  |  | Notes/assumptions
| Total incremental cost | $ | 2255120.8316
| Connection charge | $ |  | 2144000
Other charges (not part of the connection charge) for Variant 3a
| Type of charge | Unit |  | Charge | Description |  |  |  | Notes/assumptions
| Total pioneer scheme charge | $ |  | 0 | Total contribution paid by connecting party to pioneer scheme (if applicable). |  |  |  | Not applicable to Scenario 3 variants.
| Connection fees | $ |  | 9540 | Fees based on the cost of administering the connection process.
3. Incremental cost and connection charge for all Scenario 3 variants
| Incremental cost and connection charge | Unit | Variant 3a | Variant 3b | Variant 3c | Variant 3d | Description |  |  | Notes/assumptions
| Incremental cost (IC) | $ | 2255120.8316 | 6619822.9274 | 1995120.8316 | 2275120.8316 | Equal to the sum of the MS/MFS extension cost (EC), MS/MFS capacity cost (NCC), CSE extension cost, CSE capacity cost, ITC (if applicable), LHCR (if applicable), OCL (if applicable), and incremental extension cost associated with generation (if applicable) less ACOD (if applicable).
| Connection charge (CC) | $ | 2144000 | 3289337.2073 | 1884000 | 2164000 | Equal to the sum of the MS/MFS charge (posted or otherwise), the CSE cost (excluding the capacity cost if capacity costs are not allocated), up-front charge for ITC (if applicable), the LHCR (if applicable), and any charge for the incremental extension cost associated with generation (if applicable), less any reduction in charge due to ACOD (if applicable).
| Upstream capacity cost allocation |  | Variant 3a | Variant 3b | Variant 3c | Variant 3d | Notes/assumptions
| Is the customer allocated upstream capacity costs? |  | Yes | Yes | Yes | Yes | If yes, must use posted capacity rates to determine capacity cost (unless criteria for using a modified capacity rate or a share of actual project costs is met).
4. Minimum scheme/minimum flexi scheme calculations for all Scenario 3 variants
Calculation of minimum scheme/minimum flexi scheme cost
Minimum scheme/minimum flexi scheme extension cost (EC) calculation
|  |  | Variant 3a | Variant 3b | Variant 3c | Variant 3d | Notes/assumptions
| Has the customer requested a flexi scheme? |  | No | No | No | No | Minimum flexi scheme only needs to be costed if customer requests minimum flexi scheme. If minimum flexi scheme is not requested then minimum flexi scheme cost components are shaded dark grey (as not applicable).
| Components of minimum scheme cost | Unit | Variant 3a | Variant 3b | Variant 3c | Variant 3d | Notes/assumptions
| 11 kV Switchgear | $ | 119000 | 119000 | 119000 | 119000 | Schneider GHA switchgear 11 kV
| 11 kV Cable | $ | 7000 | 7000 | 7000 | 7000 | $140/m 300mm2 3c AL XPLE. Assumed 50 m for variant 3a-3d 50 x 2 for 3e
| RMU | $ | 78000 | 78000 | 78000 | 78000 | RMU from ABB
| 11/33 kV Transformer | $ |  | 2157000 |  |  | 15 MVA 33/11 kV Ground Transformer
| 33 kV Feeder Overhead Line | $ |  | 315000 |  |  | $35/m including installs (Simplex sulfur AAAC conductor). Assumed 3 kms * 3 phase
| 33 kV Pole/Cross Arm | $ |  | 86400 |  |  | 1 pole per 500 m. $14400/pole * 6. The cost is inclusive of a fully dressed pole and cable termination equipment.
| 33 kV Switchgear | $ |  | 288000 |  |  | Schneider GHA switchgear 33 kV (2 panels).
| Total minimum scheme cost | $ | 204000 | 3050400 | 204000 | 204000
| Components of minimum flexi scheme cost | Unit | Variant 3a | Variant 3b | Variant 3c | Variant 3d | Notes/assumptions
$
$
$
| Total minimum flexi scheme cost | $ | 0 | 0 | 0 | 0
Minimum scheme/minimum flexi scheme capacity cost (NCC) calculation
|  | Unit | Variant 3a | Variant 3b | Variant 3c | Variant 3d | Notes/assumptions
| Network costing zone | zone | Urban | Urban | Urban | Urban | Distributor may segment their network into network costing zones.
| Capacity cost | Unit | Variant 3a | Variant 3b | Variant 3c | Variant 3d | Notes/assumptions
| Low voltage mains (LV) | $/kVA | 240 | 240 | 240 | 240 | Capacity costs (by network tier) are pulled from the 'Network costing zones' tab. A distributor can set a posted capacity rate to zero (for any tier) where there is no foreseeable upgrade needed.
| Distribution substation (DS) | $/kVA | 600 | 600 | 600 | 600
| High voltage feeder (HVF) | $/kVA | 85 | 85 | 85 | 85
| Zone substation (ZS) | $/kVA | 380 | 380 | 380 | 380
| Sub-transmission line (STL) | $/kVA | 140 | 140 | 140 | 140
| Capacity demand - minimum scheme/minimum flexi scheme | Unit | Variant 3a | Variant 3b | Variant 3c | Variant 3d | Notes/assumptions
| Low voltage mains (LV) | kVA | 0 | 0 | 0 | 0 | Demand assumptions allow for diversity.
| Distribution substation (DS) | kVA | 0 | 0 | 0 | 0
| High voltage feeder (HVF) | kVA | 0 | 0 | 0 | 0
| Zone substation (ZS) | kVA | 4000 | 0 | 4000 | 4000
| Sub-transmission line (STL) | kVA | 3000 | 0 | 3000 | 3000
| Can estimated capacity upgrade costs be used |  | Variant 3a | Variant 3b | Variant 3c | Variant 3d | Notes/assumptions
Is the demand increment from the project more than 80% of the nominal capacity increment for:
| the high voltage feeder (HVF) tier? |  | N/A | N/A | N/A | N/A | If yes, can use estimated capacity upgrade costs for the HVF tier instead of the posted capacity rate.
| the zone substation (ZS) tier? |  | No | N/A | No | No | If yes, can use estimated capacity upgrade costs for the ZS tier instead of the posted capacity rate.
| the sub-transmission line (STL) tier? |  | No | N/A | No | No | If yes, can use estimated capacity upgrade costs for the STL tier instead of the posted capacity rate.
If yes, what is the estimated capacity upgrade costs?
| the high voltage feeder (HVF) tier? | $
| the zone substation (ZS) tier? | $
| the sub-transmission line (STL) tier? | $
| Can modified capacity rates be used |  | Variant 3a | Variant 3b | Variant 3c | Variant 3d | Notes/assumptions
Is the cost per unit of the upgrade project estimated to be more than 150%, or lower than 80%, of the applicable posted capacity rate for:
| the high voltage feeder (HVF) tier? |  | N/A | N/A | N/A | N/A | N/A if estimated capacity upgrade costs can be used (see above) or if there is no capacity demand at that tier. If yes, can use estimated capacity rate rather than posted capacity rate.
| the zone substation (ZS) tier? |  | No | N/A | No | No | N/A if estimated capacity upgrade costs can be used (see above) or if there is no capacity demand at that tier. If yes, can use estimated capacity rate rather than posted capacity rate.
| the sub-transmission line (STL) tier? |  | No | N/A | No | No | N/A if estimated capacity upgrade costs can be used (see above) or if there is no capacity demand at that tier. If yes, can use estimated capacity rate rather than posted capacity rate.
If yes, what is the estimated cost per unit relative to the posted rate for:
| the high voltage feeder (HVF) tier? | % |  |  |  |  | Needs to be greater than 150% (if cost per unit is higher than average) or less than 80% (if cost per unit is lower than average). Cell will be dark grey if not applicable (when the cost per unit of the upgrade project is between 80% and 150% of the applicable posted capacity rate OR if estimated capacity upgrade costs can be used).
| the zone substation (ZS) tier? | %
| the sub-transmission line (STL) tier? | %
| Calculation of upstream capacity cost - minimum scheme/minimum flexi scheme | Unit | Variant 3a | Variant 3b | Variant 3c | Variant 3d | Notes/assumptions
| Low voltage mains (LV) | $ | 0 | 0 | 0 | 0 | The capacity cost for a tier (if the tier is required by the connection) is the posted capacity rate multiplied by the capacity demand for the relevant tier. Estimated capacity upgrade costs or estimated capacity rates can be used when specific criteria are met, but the variants in Scenario 3 do not meet these criteria (see variant 2a for an example of these criteria applying).
| Distribution substation (DS) | $ | 0 | 0 | 0 | 0
| High voltage feeder (HVF) | $ | 0 | 0 | 0 | 0
| Zone substation (ZS) | $ | 1520000 | 0 | 1520000 | 1520000
| Sub-transmission line (STL) | $ | 420000 | 0 | 420000 | 420000
| Total upstream capacity cost (minimum scheme/minimum flexi scheme only) | $ | 1940000 | 0 | 1940000 | 1940000
Minimum scheme/minimum flexi scheme charge
| Minimum scheme/minimum flexi scheme charge | Unit | Variant 3a | Variant 3b | Variant 3c | Variant 3d | Notes/assumptions
| What is the connection charge for the minimum scheme/minimum flexi scheme? | $ | 2144000 | 3050400 | 2144000 | 2144000 | Either applied to minimum scheme or minimum flexi scheme (whichever is relevant). For Scenario 3 variants we have assumed that the distributor and connection applicant agree to recover all up-front costs through up-front connection charges.
5. Customer-selected enhancement calculations for all Scenario 3 variants
Customer-selected enhancement extension component
| Components of CSE extension cost | Unit | Variant 3a | Variant 3b | Variant 3c | Variant 3d | Notes/assumptions
$
$
| Total CSE extension cost | $ | 0 | 0 | 0 | 0
Customer-selected enhancement capacity cost component
|  | Unit | Variant 3a | Variant 3b | Variant 3c | Variant 3d | Notes/assumptions
| Network costing zone | zone | Urban | Urban | Urban | Urban | Same network costing zones as used for minimum scheme/minimum flexi scheme above.
| Capacity cost | Unit | Variant 3a | Variant 3b | Variant 3c | Variant 3d | Notes/assumptions
| Low voltage mains (LV) | $/kVA | 240 | 240 | 240 | 240 | Capacity costs (by network tier) are pulled from the 'Network costing zones' tab. A distributor can set a posted capacity rate to zero (for any tier) where there is no foreseeable upgrade needed.
| Distribution substation (DS) | $/kVA | 600 | 600 | 600 | 600
| High voltage feeder (HVF) | $/kVA | 85 | 85 | 85 | 85
| Zone substation (ZS) | $/kVA | 380 | 380 | 380 | 380
| Sub-transmission line (STL) | $/kVA | 140 | 140 | 140 | 140
| Capacity demand - customer-selected enhancement | Unit | Variant 3a | Variant 3b | Variant 3c | Variant 3d | Notes/assumptions
| Low voltage mains (LV) | kVA |  |  |  |  | Demand assumptions allow for diversity. This is the incremental demand for the customer-selected enhancement (ie, over-and-above the demand under the minimum scheme or minimum flexi scheme).
| Distribution substation (DS) | kVA
| High voltage feeder (HVF) | kVA
| Zone substation (ZS) | kVA
| Sub-transmission line (STL) | kVA
| Calculation of upstream capacity cost - CSE | Unit | Variant 3a | Variant 3b | Variant 3c | Variant 3d | Notes/assumptions
| Low voltage mains (LV) | $ | 0 | 0 | 0 | 0 | The capacity cost allocation for a tier (if the tier is required by the connection) is the posted capacity rate multiplied by the incremental capacity demand for the relevant tier for the customer-selected enhancment.
| Distribution substation (DS) | $ | 0 | 0 | 0 | 0
| High voltage feeder (HVF) | $ | 0 | 0 | 0 | 0
| Zone substation (ZS) | $ | 0 | 0 | 0 | 0
| Sub-transmission line (STL) | $ | 0 | 0 | 0 | 0
| Total upstream capacity cost - CSE | $ | 0 | 0 | 0 | 0
6. Other cost and charge calculations for all Scenario 3 variants
Incremental transmission cost (ITC)
|  | Unit | Variant 3a | Variant 3b | Variant 3c | Variant 3d | Description |  |  | Notes/assumptions
| Total incremental transmission cost (ITC) | $ | 0 | 1907839.6685 | 0 | 0 | Step change in transmission costs due to connection, including physical works to grid connections, and certain repricing events. Only applicable to certain large connections. |  |  | ITC only applicable to variant 3b. See '3b. ITC calcs' tab for ITC calculations.
| Incremental transmission cost recovered through connection charge | $ | 0 | 238937.2073 | 0 | 0 | The portion of ITC recovered through the connection charge. The remainder of ITC is recovered through ongoing charges. |  |  | ITC only applicable to variant 3b. We have assumed that the (present value of) the cost of GXP works ($239k for variant 3b) is recovered through the connection charge and (the present value) of pricing-related ITC (the remainder of the ITC) is recovered through annual charges. See '3b. ITC calcs' tab for ITC calculations.
Localised historical cost recovery (LHCR)
|  | Unit | Variant 3a | Variant 3b | Variant 3c | Variant 3d | Description |  |  | Notes/assumptions
| Localised historical cost recovery (LHCR) | $ | 0 | 0 | 0 | 0 | Total contribution paid by connecting party to localised historical cost recovery. |  |  | Not applicable to Scenario 3 variants.
Operating cost loading
|  | Unit | Variant 3a | Variant 3b | Variant 3c | Variant 3d | Description |  |  | Notes/assumptions
| Operating cost loading (OCL) | $ | 111120.8316 | 1661583.2588 | 111120.8316 | 111120.8316 | Addition to distributor's operating costs due to the new connection. Only relevant for large connections. |  |  | For Scenario 3 variants, we have assumed that the distributor estimates an operating cost equivalent to 5% of the up-front extension asset cost each year. Sums the NPV of annual opex for the connection for all years in the revenue life. OCL is calculated in the 'Reconciliation model' spreadsheet.
Injection costs and benefits
|  |  | Variant 3a | Variant 3b | Variant 3c | Variant 3d | Notes/assumptions
| Will the connection include generation? |  | No | No | Yes | Yes
Incremental cost associated with generation
Note: the components listed here are any additional components required to support injection requirements at the connection. Does not include components required for minimum scheme (or minimum flexi scheme) and other enhancements.
| Incremental components required for injection | Unit | Variant 3a | Variant 3b | Variant 3c | Variant 3d | Notes/assumptions
| Protection Panel | $ |  |  |  | 20000 | Price including fibre connection between the two sites.Not required for variant 3c because only a small injection.
$
| Total incremental costs associated with generation | $ | 0 | 0 | 0 | 20000
Avoided cost of distribution (ACOD)
|  | Unit | Variant 3a | Variant 3b | Variant 3c | Variant 3d | Notes/assumptions
| Network costing zone | zone | N/A | N/A | Urban | Urban | Same network costing zones as used for minimum scheme/minimum flexi scheme and customer-selected enhancement above.
| Capacity cost | Unit | Variant 3a | Variant 3b | Variant 3c | Variant 3d | Notes/assumptions
| Low voltage mains (LV) | $/kVA |  |  | 240 | 240 | Capacity costs (by network tier) are pulled from the 'Network costing zones' tab. A distributor can set a posted capacity rate to zero (for any tier) where there is no foreseeable upgrade needed.
| Distribution substation (DS) | $/kVA |  |  | 600 | 600
| High voltage feeder (HVF) | $/kVA |  |  | 85 | 85
| Zone substation (ZS) | $/kVA |  |  | 380 | 380
| Sub-transmission line (STL) | $/kVA |  |  | 140 | 140
| Injection | Unit | Variant 3a | Variant 3b | Variant 3c | Variant 3d | Notes/assumptions
| Low voltage mains (LV) | kVA |  |  | 0 | 0
| Distribution substation (DS) | kVA |  |  | 0 | 0
| High voltage feeder (HVF) | kVA |  |  | 0 | 0
| Zone substation (ZS) | kVA |  |  | 500 | 0 | Variant 3d is not expected to provide any avoided capacity cost benefits at ZS or STL tier.
| Sub-transmission line (STL) | kVA |  |  | 500 | 0
| Calculation of avoided cost of distribution (ACOD) | Unit | Variant 3a | Variant 3b | Variant 3c | Variant 3d | Notes/assumptions
| Low voltage mains (LV) | $ |  |  | 0 | 0
| Distribution substation (DS) | $ |  |  | 0 | 0
| High voltage feeder (HVF) | $ |  |  | 0 | 0
| Zone substation (ZS) | $ |  |  | 190000 | 0
| Sub-transmission line (STL) | $ |  |  | 70000 | 0
| Total avoided cost of distribution (ACOD) | $ | 0 | 0 | 260000 | 0
Pioneer scheme charge
Note: is not part of the connection charge
| Type of charge | Unit | Variant 3a | Variant 3b | Variant 3c | Variant 3d | Description |  |  | Notes/assumptions
| Total pioneer scheme charge | $ | 0 | 0 | 0 | 0 | Total contribution paid by connecting party to pioneer scheme. |  |  | Not applicable to Scenario 3 variants.
Connection fees
Note: is not part of the connection charge and excludes any adminstration fee for a pioneer scheme
| Type of fee | Unit | Variant 3a | Variant 3b | Variant 3c | Variant 3d | Description |  |  | Notes/assumptions
| Application processing | $ | 7690 | 7690 | 7690 | 7690 | Application processing fee based on the costs of administering the connection process. |  |  | We have based on fees in Part 6 of the Code, but this is not a requirement.
| Technical observation | $ | 1850 | 1850 | 1850 | 1850 | Technical observation fee based on the csots of adminisering the connection process. |  |  | We have based on fees in Part 6 of the Code, but this is not a requirement.
| Total fees | $ | 9540 | 9540 | 9540 | 9540

## 1f. Pioneer scheme
Pioneer scheme calculations | [5 empty] | key | input | linked | calculated | selection | set number
Variant 1f pioneer scheme
Note that connection party 4 is the connecting party for the purposes of variant 1f. For simplicity, the calculations below assume that the pioneer scheme is set up in December 2025 and CPI inflation is 2% every year. This technically means that connection party 4 connects in December 2030 (5 years after the pioneer scheme is set up) - this is inconsistent with assumptions we make elsewhere (largely in the reconciliation spreadsheet) where we assume the connection occurs in the year ending 31 March 2026. However, this sheet is just intended to show how pioneer scheme calculations could be made (noting a distributor has some flexibility in determining how pioneer contributions are calcuated) and the numbers are illustrative. The only numbers from this sheet that feed into the worked example calculations for variant 1f in the '1. small connection' tab are the contribution paid by connection party 4 and the administration fee.
Pioneer scheme information
| Pioneer scheme set-up information | Unit | Value | Description |  |  | Notes/assumptions
| Opening value | $ | 80000 | Value of the pioneer’s contribution to the cost of the pioneering connection works.
| Scheme duration | years | 7 |  |  |  | Default value. Must not be less than 7 years.
| Depreciation duration | years | 20 |  |  |  | Required duration set in Code.
| Total length | m | 600 | Length of LV mains funded by the pioneer.
| Thresholds | Unit | Value | Description |  |  | Notes/assumptions
| Threshold to require contribution (after deducting fee) | $ | 1000 | A pioneer scheme contribution must not be collected if the contribution would be less than this threshold in December 2025 dollars after deducting any fee to cover the reasonable costs of administering the scheme. Adjusted each year by CPI movement. |  |  | Threshold set in Code.
| Threshold to be a pioneer | $ | 25000 | Any connection applicant who subsequently connects to a pioneering connection works is a subsequent pioneer if they make a pioneer scheme contribution of more than this threshold in December 2025 dollar terms. Adjusted each year by CPI movement. |  |  | Threshold set in Code. Subsequent pioneers are paid a share of any subsequent pioneer scheme contributions collected (after any fee to cover costs of administering the scheme are deducted).
| Fee | Unit | Value | Description |  |  | Notes/assumptions
| Administration fee | $ | 250 | Deducted from any contribution to the pioneer scheme before the contribution is distributed among existing pioneers.
| Inflation adjustment | Unit | Value | Description |  |  | Notes/assumptions
| CPI inflation | % | 2% | Inflation rate used to adjust values to December 2025 dollars. |  |  | Have assumed CPI inflation is 2% in all years for simplicity.
Calcuation of contributions
Connection party 4 is the connection party for the purposes of variant 1f.
|  | Unit | Connection party 1 = first pioneer | Connection party 2 | Connection party 3 | Connection party 4 | Description |  |  | Notes/assumptions
| Years since opening | Years | 0 | 0.5 | 2 | 5
| Current value of pioneer scheme | $ | 80000 | 78000 | 72000 | 60000 | Opening value depreciated by 5% per annum (20 year depreciation duration with straight line depreciation).
| Distance | km | 600 | 550 | 500 | 300 | Distance of the connection along the length of the extension. |  |  | Maximum value is 6km (for this example) because the total length of the extension is 6km.
| Distance ratio | % | 100% | 91.67% | 83.33% | 50% | Distance of the connection along the length of the extension relative to the total length of the extension.
| Capacity demand | kVA | 4 | 4 | 4 | 4 |  |  |  | Capacity demand at LV tier.
| Capacity ratio | % | 100% | 50% | 33.33% | 25% | Capacity demand of connection relative to demand of all connections.
| Contribution | $ | 80000 | 35750 | 20000 | 7500 | Contribution to the pioneer scheme by the connection. Distributor must take into account shares of extension length and capacity of the pioneer scheme when determining a contribution. |  |  | Code does not define how share of extension length and capacity must be taken into account. We have assumed that a contribution is calculated as: current value x distance ratio x capacity ratio.
|  | Unit | Connection party 1 = first pioneer | Connection party 2 | Connection party 3 | Connection party 4 | Description |  |  | Notes/assumptions
| Threshold to require contribution (before deducting fee) | $ | 1250 | 1262.4381 | 1300.5 | 1380.101 | Equal to threshold set in Code plus administration fee, adjusted each year by CPI movement.
| Is the connecting party required to make a contribution? |  | Yes | Yes | Yes | Yes |  |  |  | Connection party is required to make a contribution if the contribution would be greater than the threshold set in the Code plus any fee charged to cover reasonable costs of administering the scheme.
|  | Unit | Connection party 1 = first pioneer | Connection party 2 | Connection party 3 | Connection party 4 | Description |  |  | Notes/assumptions
| Threshold to be a pioneer | $ | 25000 | 25248.7623 | 26010 | 27602.0201 | Equal to threshold set in Code , adjusted each year by CPI movement.
| Is the connecting party a pioneer? |  | Yes | Yes | No | No |  |  |  | Connection parties 3 and 4 are not pioneers (as their contribution is less than the threshold) and therefore won't receive a share of any contributions paid by subsequent connection parties.
Distribution of contributions
| First party connects | Unit | Connection party 1 = first pioneer | Connection party 2 | Connection party 3 | Connection party 4 | Sum | Description |  |  | Notes/assumptions
| Opening contribution | $ | 80000 |  |  |  | 80000 | Opening contribution paid by first pioneer.
| Second party connects | Unit | Connection party 1 = first pioneer | Connection party 2 | Connection party 3 | Connection party 4 | Sum | Description |  |  | Notes/assumptions
| Contribution paid by connection party 2 | $ |  | 35750 |  |  |  | Connection party 2's contribution
| Rebate to pioneers | $ | -35500 |  |  |  |  | The first pioneer is paid connection party 2's contribution less the administration fee.
| Balance of pioneer(s) contribution | $ | 44500 | 35750 |  |  | 80250 | The contribution that each pioneer has made to the costs of the pioneering connection works.
| Third party connects | Unit | Connection party 1 = first pioneer | Connection party 2 | Connection party 3 | Connection party 4 | Sum | Description |  |  | Notes/assumptions
| Contribution paid by connection party 3 | $ |  |  | 20000 |  |  | Connection party 3's contribution
| Rebate to pioneers | $ | -10951.7134 | -8798.2866 |  |  |  | The first pioneer and connection party 2 (also a pioneer) are paid shares of connection party 3's contribution less the administration fee. Distributed in proportion to balances.
| Balance of pioneer(s) contribution | $ | 33548.2866 | 26951.7134 | 0 |  | 60500 | The contribution that each pioneer has made to the costs of the pioneering connection works. |  |  | Equal to zero for connection party 3 because they are not a pioneer.
| Fourth party connects | Unit | Connection party 1 = first pioneer | Connection party 2 | Connection party 3 | Connection party 4 | Sum | Description |  |  | Notes/assumptions
| Contribution paid by connection party 4 | $ |  |  |  | 7500 |  | Connection party 4's contribution
| Rebate to pioneers | $ | -4020.2492 | -3229.7508 | 0 |  |  | The first pioneer and connection party 2 (also a pioneer) are paid shares of connection party 4's contribution less the administration fee. Distributed in proportion to balances. Connection party 3 is not paid a share of the contribution as they did not met the threshold to be a pioneer.
| Balance of pioneer(s) contribution | $ | 29528.0374 | 23721.9626 | 0 | 0 | 53250 | The contribution that each pioneer has made to the costs of the pioneering connection works. |  |  | Equal to zero for connection parties 3 and 4 because they are not pioneers.
| Share of contributions by pioneers | % | 55.45% | 44.55%

## 1g. Local hist cost recovery
Localised historical cost recovery calculations | [5 empty] | key | input | linked | calculated | selection | set number
Variant 1g localised historical cost recovery
Note that connection party 4 is the connecting party for the purposes of variant 1f. For simplicity, the calculations below assume that the pioneer scheme is set up in December 2025 and CPI inflation is 2% every year. This technically means that connection party 4 connects in December 2030 (5 years after the pioneer scheme is set up) - this is inconsistent with assumptions we make elsewhere (largely in the reconciliation spreadsheet) where we assume the connection occurs in the year ending 31 March 2026. However, this sheet is just intended to show how pioneer scheme calculations could be made (noting a distributor has some flexibility in determining how pioneer contributions are calcuated) and the numbers are illustrative. The only numbers from this sheet that feed into the worked example calculations for variant 1f in the '1. small connection' tab are the contribution paid by connection party 4 and the administration fee.
Localised historical cost recovery information
| Localised historical cost recovery set-up information | Unit | Value | Description |  |  | Notes/assumptions
| Original cost | $ | 120000 | Cost of the original network development.
| Number of connections | # | 6 | Number of connections required to paid a contribution to the localised historical cost recovery.
| Allocation per connection | $ | 20000 | Value of contribution required from each connection party. Equal to original cost divided by number of connections. Allocation will be adjusted by CPI movement.
| Inflation adjustment | Unit | Value | Description |  |  | Notes/assumptions
| CPI inflation | % | 2% | Inflation rate used to adjust values to December 2025 dollars. |  |  | Have assumed CPI inflation is 2% in all years for simplicity.
Calcuation of contributions
Connection party 1 is the connection party for the purposes of variant 1g.
|  | Unit | Connection party 1 | Connection party 2 | Connection party 3 | Connection party 4 | Connection party 5 | Connection party 6 | Connection party 7 | Description |  | Notes/assumptions
| Party | # | 1 | 2 | 3 | 4 | 5 | 6 | 7
| Year of connection | Year | 0 | 1 | 1 | 4 | 6 | 9 | 10
| Contribution | $ | 20000 | 20400 | 20400 | 21648.6432 | 22523.2484 | 23901.8514 | 0 | Contribution by each connection party to the original cost (adjusted for CPI inflation). |  | Connection party 7 is not required to make a contribution because the local historical cost recovery was set up to recover the original cost from only the first six connecting parties.

## 3b. ITC calcs
Incremental transmission cost calculations for variant 3b | [5 empty] | key: | input | linked | calculated | selection | set number
Calculation of ITC for variant 3b
| Discount rate calculation | Unit |  | Description |  |  |  | Notes/assumptions
| Mid-point vanilla WACC for EDBs | % | 6.53% | Most recently available mid-point estimate of vanilla WACC (weighted average cost of capital) made by the Commerce Commission. |  |  |  | Mid-point vanilla WACC for EDBs from May 2025 determination.
| Forecast annual CPI inflation for year to 1 June | % | 1.9% | Inflation projection for the year ahead from the most recent Monetary Policy Statement (MPS) published by the Reserve Bank of New Zealand. |  |  |  | Forecast annual CPI inflation from the May 2025 MPS for the year to 1 June 2026.
| Discount rate real | % | 4.63% | Used to make compounding downward adjustments to revenue from future years. Is equal to the most recently available mid-point estimate of vanilla WACC less an adjustment to remove inflation. |  |  |  | Needs to be updated annually. Is not distributor-specific.
|  | Unit | Description |  |  |  | Notes/assumptions |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
| Pricing year | year | Year starting 1 April. | [7 empty] | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
| Discount factor | # | Discount factor to adjust revenue to present value. |  |  |  | Discount factor is the same for all variants and for both distribution and transmission revenue. |  |  |  | 1 | 0.95575 | 0.91346 | 0.87303 | 0.8344 | 0.79748 | 0.76219 | 0.72846 | 0.69623 | 0.66542 | 0.63597 | 0.60783 | 0.58093 | 0.55523 | 0.53066 | 0.50717
| Transmission revenue adjustment factor (real) | # | Used to adjust first-year transmission revenue figure for overall movements in target revenue (which, all things being equal, will flow into lines charges). |  |  |  | Have assumed the connection is livened and starts to produce transmission revenue sometime during the 12-month period starting 1 April 2025.Based on Wellington Electricity figures. Needs to be updated annually. |  |  |  | 1 | 1.15 | 1.16 | 1.19 | 1.21 | 1.24 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
| Cost of GXP works | $ | [8 empty] | 1 2027: 250000
| Connection charge uplift | $ | [9 empty] | 10000 | 10086.9565 | 10347.8261 | 10521.7391 | 10782.6087 | 10434.7826 | 10434.7826 | 10434.7826 | 10434.7826 | 10434.7826 | 10434.7826 | 10434.7826 | 10434.7826 | 10434.7826 | 10434.7826
| Benefit-based charge adjustment | $ | [9 empty] | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000
| Step change in cost allocation | $ | [13 empty] | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000
| Adjusted incremental transmission cost (PV) | $ | [8 empty] | 0 | 324954.6019 | 82290.4551 | 78876.7543 | 75531.4788 | 152144.9901 | 145147.287 | 138724.3496 | 132585.6347 | 126718.5651 | 121111.1203 | 115751.8114 | 110629.6582 | 105734.1663 | 101055.3057 | 96583.4901
|  | Unit | Variant 3b | Description | Source | Assumption |  | Notes/assumptions
| Total incremental transmission cost (ITC) | $ | 1907839.6685
Calculation of ITC recovered through connection charge
|  | Unit | Variant 3b | Description | Source | Assumption |  | Notes/assumptions
| GXP works (PV) | $ | 238937.2073
Calculation of ITC recovered through incremental revenue
|  | Unit | Description |  |  |  | Notes/assumptions |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
| Incremental transmission costs recovered through annual charges (PV) | $ | [8 empty] | 0 | 86017.3946 | 82290.4551 | 78876.7543 | 75531.4788 | 152144.9901 | 145147.287 | 138724.3496 | 132585.6347 | 126718.5651 | 121111.1203 | 115751.8114 | 110629.6582 | 105734.1663 | 101055.3057 | 96583.4901
|  | Unit | Variant 3b | Description | Source | Assumption |  | Notes/assumptions
| Total incremental transmission costs recovered through annual charges (PV) | $ | 1668902.4612

## Network costing zones
Unit capacity costs by network costing zone |  | key | input | linked | calculated | selection | set number
All $ inputs are real 2025
| Description | Unit | Urban | Rural A | Rural B | Notes/assumptions
Unit capacity cost - LV | Unit cost for incremental low voltage mains (LV) capacity | $/kVA | 240 | 0 | 170 | Capacity costs are based on rates in Network Capacity Rates Guidance. Urban rates are close to the averages of 'Auckland Urban' and 'Northern Urban' rates. Rural rates (A and B) are close to the 'Rural' rates in the guidance, but we have zero-rated capacity for rural LV mains and distributions substations in 'Rural A' to reflect these components having sufficient capacity that the distributor thinks they are unlikely to run out of capacity within their network planning horizon.
Unit capacity cost - DS | Unit cost for incremental distribution substation (DS) capacity | $/kVA | 600 | 0 | 530
Unit capacity cost - HVF | Unit cost for incremental high voltage feeder (HVF) capacity | $/kVA | 85 | 85 | 85
Unit capacity cost - ZS | Unit cost for incremental zone substation (ZS) capacity | $/kVA | 380 | 380 | 380
Unit capacity cost - STL | Unit cost for incremental sub-transmission line (STL) capacity | $/kVA | 140 | 100 | 100

## List
List for data validation
Yes
No
N/A