## Network Costing Zones
| Description | Unit | Standard - Metro | Standard - Urban | Standard - Rural
Capacity cost - LV | Unit cost for incremental low voltage mains (LV) capacity | $/kVA | 266.3333 | 219.1667 | 171
Capacity cost - DS | Unit cost for incremental distribution substation (DS) capacity | $/kVA | 598.5333 | 606.7 | 531.6667
Capacity cost - HVF | Unit cost for incremental high voltage feeder (HVF) capacity | $/kVA | 85.0333 | 85.8667 | 84.6667
Capacity cost - ZS | Unit cost for incremental zone substation (ZS) capacity [Case 1A] | $/kVA | 455.2 | 455.2 | 455.2
Capacity cost - ZS | Unit cost for incremental zone substation (ZS) capacity [Case 1B] | $/kVA | 227.6667 | 227.6667 | 227.6667
Capacity cost - ZS | Unit cost for incremental zone substation (ZS) capacity [Case 2] | $/kVA | 462.4 | 462.4 | 462.4
Capacity cost - ZS | Unit cost for incremental zone substation (ZS) capacity [Case 3] | $/kVA | 220.7333 | 220.7333 | 220.7333
Capacity cost - STL | Unit cost for incremental sub-transmission line (STL) capacity [Case 1] | $/kVA | 181.2 | 132.7 | 84.2
Capacity cost - STL | Unit cost for incremental sub-transmission line (STL) capacity [Case 2] | $/kVA | 120.7692 | 120.7692 | 120.7692

## Base Rate
Connection Level | Scenarios | Network Component |  | Assumptions | Number of Unit |  | Unit Cost | UOM | Total Cost | Notes
[LV] LV Mains (400 V) | [Case 1] New LV connection | 1 | LV overhead conductor | Typical OHL Length in rural area, NEXANS 95mm2 Al ABC / Fluorine AAAC | 300 | m | 60 | m | 18000 | $15 per phase x 4 (3Ph+N)
|  | 2 | Pole/Cross arm (400 V) |  | 300 | m | 110 | m | 33000 | (length/100m*$6500)+(length*$4500*10days/1000m)
|  | 3 | Single Phase Pole Fuse |  | 3 | pcs | 100 | pcs | 300
|  | 4 | LV Cables | Typical cable Length in urban area, NEXANS 0.6/1 kV AL XLPE URD Cable 4x50 | 100 | m | 159 | m | 15900
|  | 5 | Service Pillar |  | 1 | pcs | 34000 | pcs | 34000
|  | 6 | Cable work | Assumed to be $3k/km | 100 | m | 300 | m | 30000
| Assumed Total Capacity | [7 empty] | 300 | kVA
| LV Mains Capacity Rate (Metro) | [7 empty] | 266.3333 | /kVA | 79900
| LV Mains Capacity Rate (Urban) | [7 empty] | 219.1667 | /kVA (assumed 100m total length, 50% OHL, 50% cable) | 65750
| LV Mains Capacity Rate (Rural) | [7 empty] | 171 | /kVA | 51300
[DT] Distribution Substation (11kV/415V) | [Case 1] New distribution substation | 1 | Transformer (ground mounted) | 300 kVA | 1 | pcs | 75000 | pcs | 75000
|  | 2 | Transformer (pole mounted) | 300 kVA | 1 | pcs | 39000 | pcs | 39000
|  | 3 | RMU | 11kV Ring Main Unit (3tier) with lockable external enclosure | 1 | pcs | 78000 | pcs | 78000
|  | 4 | 11 kV overhead conductor to the nearest RMU | Iodine AAAC (or similar for 11 kV) | 300 | m | 105 | m | 31500 | $35 per phase x 3 (3Ph)
|  | 5 | Pole/Cross arm (11 kV) |  | 100 | m | 110 | m | 11000 | (length/100m*6500)+(length*4500*10/1000)
|  | 6 | 11 kV Cable to the nearest RMU | 11kV XLPE, 3 core, 185mm2 | 100 | m | 166 | m | 16600
|  | 7 | Cable termination |  | 2 | pcs | 4980 | pcs | 9960
| Assumed Total Capacity | [7 empty] | 300 | kVA
| Distribution Substations Capacity Rate (Metro) | [7 empty] | 598.5333 | /kVA | 179560
| Distribution Substations Capacity Rate (Urban) | [7 empty] | 606.7 | /kVA | 182010
| Distribution Substations Capacity Rate (Rural) | [7 empty] | 531.6667 | /kVA | 159500
[HVF] HV Feeder (11kV) | [CASE 1] New HV feeder (radial) | 1 | RMU | 11kV Ring Main Unit (3tier) with lockable external enclosure | 1 | pcs | 78000 | pcs | 78000
|  | 2 | 11 kV overhead conductor to the nearest zone substation | Assumed length, Iodine AAAC (or similar for 11 kV ) | 2000 | m | 105 | m | 210000 | $35 per phase x 3 (3Ph)
|  | 3 | Pole/Cross arm (11 kV) |  | 2000 | m | 110 | m | 220000 | (length/100m*6500)+(length*4500*10/1000)
|  | 4 | 11 kV Cable to the nearest zone substation | Assumed length, 11kV XLPE, 3 core, 300mm2 | 2000 | m | 210 | m | 420000
|  | 5 | Cable termination |  | 2 | pcs | 6100 | pcs | 12200
| Assumed Total Capacity | [7 empty] | 6000 | kVA
| High Voltage Feeder Capacity Rate (Metro) | [7 empty] | 85.0333 | /kVA | 510200
| High Voltage Feeder Capacity Rate (Urban) | [7 empty] | 85.8667 | /kVA | 515200
| High Voltage Feeder Capacity Rate (Rural) | [7 empty] | 84.6667 | /kVA | 508000
[ZS] Zone Substation (33/11 kV) | [CASE 1A] Existing ZS extension + one transformer replacement | 1 | Land | Excluded from the calculation |  |  |  |  | 0
|  | 2 | MV switchboard (11 kV) | Single busbar |  |  |  |  | 0
|  | 2a | Incomer panel |  |  | pcs | 119000 | pcs | 0
|  | 2b | Feeder panel |  | 1 | pcs | 119000 | pcs | 119000
|  | 2c | Bus tie panel |  |  | pcs | 119000 | pcs | 0
|  | 3 | Transformer | 1 x 15 MVA transformer | 1 | pcs | 2157000 | pcs | 2157000
|  | 4 | HV switchboard (33 kV) | Single busbar gas insulated |  |  |  |  | 0
|  | 4a | Incomer panel |  |  | pcs | 144000 | pcs | 0
|  | 4b | Feeder panel |  |  | pcs | 144000 | pcs | 0
|  | 5 | Misc. panels | Control, comms, metering (lumped) |  | pcs | 25000 | pcs | 0
|  | 6 | Building | Transformer(s) located outside. (10m x 2.5m) |  | m2 | 13000 | m2 | 0
|  | Case 1A Assumed Total Capacity | [6 empty] | 5000 | kVA
|  | Case 1A Capacity Rate | [6 empty] | 455.2 | /kVA | 2276000
| [CASE 1B] New ZS with 1 Transformer | 1 | Land | Excluded from the calculation |  |  |  |  | 0
|  | 2 | MV switchboard (11 kV) | Single busbar |  |  |  |  | 0
|  | 2a | Incomer panel |  | 1 | pcs | 119000 | pcs | 119000
|  | 2b | Feeder panel |  | 3 | pcs | 119000 | pcs | 357000
|  | 2c | Bus tie panel |  | 0 | pcs | 119000 | pcs | 0
|  | 3 | Transformer | 1 x 15 MVA transformer | 1 | pcs | 2157000 | pcs | 2157000
|  | 4 | HV switchboard (33 kV) | Single busbar gas insulated |  |  |  |  | 0
|  | 4a | Incomer panel |  | 2 | pcs | 144000 | pcs | 288000
|  | 4b | Feeder panel |  | 1 | pcs | 144000 | pcs | 144000
|  | 5 | Misc. panels | Control, comms, metering (lumped) | 1 | pcs | 25000 | pcs | 25000
|  | 6 | Building | Transformer(s) located outside. (10m x 5m) | 25 | m2 | 13000 | m2 | 325000
|  | Case 1B Assumed Total Capacity | [6 empty] | 15000 | kVA
|  | Case 1B Capacity Rate | [6 empty] | 227.6667 | /kVA | 3415000
| [CASE 2] New ZS with 2 Transformers | 1 | Land | Excluded from the calculation |  |  |  |  | 0
|  | 2 | MV switchboard (11 kV) | Double busbar |  |  |  |  | 0
|  | 2a | Incomer panel |  | 2 | pcs | 119000 | pcs | 238000
|  | 2b | Feeder panel |  | 6 | pcs | 119000 | pcs | 714000
|  | 2c | Bus tie panel |  | 1 | pcs | 119000 | pcs | 119000
|  | 3 | Transformer | 2 x 15 MVA transformer | 2 | pcs | 2157000 | pcs | 4314000
|  | 4 | HV switchboard (33 kV) | Single busbar gas insulated |  |  |  |  | 0
|  | 4a | Incomer panel |  | 2 | pcs | 144000 | pcs | 288000
|  | 4b | Feeder panel |  | 2 | pcs | 144000 | pcs | 288000
|  | 5 | Misc. panels | Control, comms, metering (lumped) | 1 | pcs | 25000 | pcs
|  | 6 | Building | Transformer(s) located outside (10m x 7.5m) | 75 | m2 | 13000 | m2 | 975000
|  | Case 2 Assumed Total Capacity | [6 empty] | 15000 | kVA
|  | Case 2 Capacity Rate | [6 empty] | 462.4 | /kVA | 6936000
| [CASE 3] Extend ZS from 2 to 3 Transformers | 1 | Land | Excluded from the calculation |  |  |  |  | 0
|  | 2 | MV switchboard (11 kV) | 3 bus sections |  |  |  |  | 0 | 3 x (1incomer 3 feeders) + 2 bus tie
|  | 2a | Incomer panel |  | 1 | pcs | 119000 | $/pcs | 119000
|  | 2b | Feeder panel |  | 3 | pcs | 119000 | $/pcs | 357000
|  | 2c | Bus tie panel |  | 1 | pcs | 119000 | $/pcs | 119000
|  | 3 | Transformer | 1 x 15 MVA transformer | 1 | pcs | 2157000 | $/pcs | 2157000
|  | 4 | HV switchboard (33 kV) | Single busbar gas insulated |  |  |  |  | 0 | 2 incomers 3 feeders
|  | 4a | Incomer panel |  | 0 | pcs | 144000 | $/pcs | 0
|  | 4b | Feeder panel |  | 1 | pcs | 144000 | $/pcs | 144000
|  | 5 | Misc. panels | Control, comms, metering (lumped) | 1 | pcs | 25000 | $/pcs | 25000
|  | 6 | Building | Transformer(s) located outside (10m x 10m) | 30 | m2 | 13000 | $/m2 | 390000 | Building modifications only
|  | Case 3 Assumed Total Capacity | [6 empty] | 15000 | kVA
|  | Case 3 Capacity Rate | [6 empty] | 220.7333 | /kVA | 3311000
[STL] Sub Transmission line (33 kV) | [CASE 1] New sub transmission line to a GXP - 100% OHL | 1 | 33 kV overhead line | Typical length, Selenium AAAC conductor | 10000 | m | 105 | m | 1050000 | 3 x $35 for 3ph
|  | 2 | Overhead pole |  | 10000 | m | 82.5 | m | 825000 | (length/200m*7500)+(length*4500*10/1000)
|  | 3 | Cable | 33 kV 400 mm2 AL (10 kA / 1s) | 10000 | m | 130 | m | 1300000
|  | 4 | Additional HV switchboard at the GXP |  | 1 | pcs | 230000 | $/pcs | 230000
|  | 5 | Cable work |  | 10000 | m | 300 | m | 3000000
|  | Case 1 Assumed Total Capacity | [6 empty] | 25000 | kVA
|  | Sub Transmission Line Capacity Rate (Metro) | [6 empty] | 181.2 | /kVA | 4530000
|  | Sub Transmission Line Capacity Rate (Urban) | [6 empty] | 132.7 | /kVA | 3317500
|  | Sub Transmission Line Capacity Rate (Rural) | [6 empty] | 84.2 | /kVA | 2105000
| [Case 2] Cutting into an existing double circuit line + new switching station | 1 | Land | Excluded |  |  |  |  | 0
|  | 2 | 33 kV switchgear | Single bus, 4 CBs | 4 | pcs | 230000 | pcs | 920000
|  | 3 | Building | 10m x 5 | 50 | m2 | 13000 | m2 | 650000
|  | Case 2 Assumed Total Capacity | [6 empty] | 13000 | kVA (assumed 38 MVA line, 25 MVA transformer)
|  | Case 2 Capacity Rate | [6 empty] | 120.7692 | $/kVA | 1570000